## MAIN SUMMARY
PHOTON - DLF CYBER CITY - HYDERABAD UNPRICED BOQ FOR INTERIOR AND MEP SERVICES
BOQ SUMMARY
S.NO | PACKAGE | AMOUNT( Rs)
1 | INTERIOR WORKS | 20485551
2 | RESTROOM FINISHES | 2511037.0663
3 | HVAC | 4698772.7
4 | LT ELECTRICAL WORKS | 8595785.94
5 | UPS
6 | FIRE SAFETY AND SECURITY SYSTEMS BOQ | 6358576.8337
7 | PHE SYSTEM BOQ | 2134411
| TOTAL ( EXCLUDING TAXES) | 44784134.54
BOCW @1% extra.
The above BOQ does not included the following
1 | cost of power and water during construction
2 | Cost of PCC screed
3 | cost of ISP, EPABX & Network active components
4 | cost of white goods and office equipment's , Kitchen equipements and appliances , Plants and planter boxes
5 | cost of AV equipment's
6 | cost of power feeders , AHU, Rising main, VFD, IBMS system and base building infrastructure works

## INTERIOR
INTERIOR WORKS
S.N0 | Description of Item | Specification | Unit | Total Qty | Rate ( Supply+ Installation) | Amount | JLL Remarks
Notes:
Below mentioned points are under Civil & Interior works vendors scope
All unnecessary holes, gaps, openings in the walls, gyp ceiling / partitions, floor etc to be filled / closed by joinery vendor. AHU room and external wall / shaft to be sealed with Aerocon wall. All external wall gap to be sealed with Fire stop / Acoustical sealant as specified.
Joinery vendor to be responsible for labor toilets – maintenance etc. (for all the agencies).
Scrapping of flooring & cleaning the floor before carpet installation. (Floor to be wet mobbed & handed over to carpet installation team).
Cleaning / painting of lobby & other builder areas which will be used by the agencies while execution.
Touch up & finishing of all the existing doors which are handed over by builder while taking the possession.
All unnecessary holes, gaps, openings in the walls, gyp ceiling / partitions, floor etc to be filled / closed by joinery vendor (in the AHU rooms, unnecessary opening of walls to be closed only by building wall & not using any other material like ply or gyp board etc).
Housekeeping ( Including housekeeping on daily basis) to be part of your quotation and will not be paid extra. General housekeeping for all other packages to be in joinery vendor scope which is indicated as separate item in BOQ
Electrical vendor to provide temp lighting for fitout execution period . Power junction boxes to be placed at every 10 meter distance with all safety norms recommended by the base builder /PM.
Note: *Vendors are requested to visit the site and quote accordingly. *Vendor shall follow safety, barricading needs to be done as per PM /Architect instruction *Site should be left clean and broom finish once work complete and every day morning before 10AM *vendors are requested to visit the site and check the availability of water, power, service lift, debris dumping yard, lighting and quote accordingly for the works mentioned below. *Vendor to the check the work timings permitted from client / builder. *Quoted rates should includes shifting, lifting, loading, unloading of materials. *Quoted rates should includes scaffolding at all heights.
All the Basic price exclusive of all the taxes,transportation charges and wastage etc..
Cost to includes creating temporary store room, Site office with temporary partition, 2 Tables and chair
Project resource details , Time line chart to be attached along with cost proposal .
Material unloading area will be allocated in the ground floor level. All materials to be dumped in the specific location identified by the base builder and PM. Debris dumping area to be covered with temporary partition and Collected debris to be disposed out of the building premises on regular basis (daily or alternative days)
All items listed below shall be executed/ installed only after mock-up/ product approval in terms of colour, design, finishes etc by Client, PMC and Architect . Shop dwg to be submitted for Fire door / Glass partition / Foldable partition / Stile Door / Factory made storages / Baffle ceiling / Cell ceiling / Moss panelling / Danoline ceiling / Tile Flooring & wall dado Joints
True ceiling height - 3600mm . Movable Aluminium ladders of 3 meter height to be installed at site with all safety signs and barricade .
Heat soaking test certificate to be provided for all the toughened glass along with the purchased quantity.
The vendor shall follow all safety guidelines as recommended by the base builder (DLF) and in accordance with Telangana State / Indian government safety regulations for construction.
All labourers working within the building premises must wear personal protective equipment (PPE), and a dedicated safety officer must be deployed by the interior vendor for day and night operations (24/7)
Any additional items required to be executed at site must be intimated to photon in advance and work to be started only after photons written approval . For non tender items, vendor to produce actual invoice and vendor margin 10% will be approved and certified by PM / Photon
The service lift is available on-site and will be permitted for use by the base builder during restricted time slots. The vendor must inspect the site and verify the details of the material loading and unloading platform. In case the service lift is unavailable or not in operative condition, the vendor shall transport materials via the staircase. No additional cost will be approved for this.
The project timeline for completion is 75 days from the date of project kick-off. The vendor must provide a milestone schedule and resource details specific to this project.
A | DEMOLITION WORKS
1 | Breaking of wall ( Toilet Work and other services) | Demolition of existing wall of any thickness inclusive of removal of existing brick wall , Aerocon wall , RCC lintels, RCC slabs, cleaning etc, & disposal of debris from building premises as per base builders guidelines. ( Existing rest room walls and counter , internal plumbing lines to be removed and debris to be cleared from the building premises) | Sqm | 220 | 371 | 81620
2 | Breaking of Existing d base PCC screed | Breaking of existing Tile Flooring and base PCC screed ( up to 70-90mm Avg depth) and cleaning & disposal of debris from building premises as per base builders guidelines | Sqm | 250 | 318 | 79500
3 | Floor grinding | Existing screed floor (where the undulations are more than 3-5mm) to be levelled with floor grinding machine as per site condition. Cost inclusive of cleaning the screed floor and clear debris from building premises as per PM directions after completion of work. | sqm | 100 | 265 | 26500
B | ANTI TERMITE TREATMENT |  |  |  | 0 | 0
1 | Anti Termite Treatment | Providing Pest control and Anti-termite treatment by appointing a specialised agency as per the specifications mentioned by the Bureau of Indian Standards and Agencies specifications (whichever is higher), for General Civil, Plumbing,/ Drainage and timber/ Carpentry works, Gypsum related work, including a 5-year guarantee under suitable undertaking on stamp paper etc, complete as directed. (Mode of measurement to be on carpet-area of floor and not the area of surface treated.) . three rounds of pest control in all areas, first round to be executed at the time of commencement of fit-out, balance to be executed during fit-out as per PM directions. | Sqm | 1275 | 90.1 | 114877.5
[5 empty] | 0 | 0
C | CIVIL & WET WORKS |  |  |  | 0 | 0
1 | POP punning | Providing and applying POP punning to walls of avg. 12mm - 15mm thickness and above to line level and plumb; required punning to be undertaken and completed in workman-like manner, to ensure desired finishing standards, as per approval(s) of the Architects. The final finish should be of a uniform and neat finish to the satisfaction of the Architect. | Sqm | 300 | 445.2 | 133560
2 | PCC Screed - 70-80 mm thk | Providing and laying PCC screed up to 70-80 mm avg Ht. of cement concrete ratio 1:3:6 (1unit cement, 3units- sand, 6units- course aggregate) in necessary level & slope, finished smoothly with 6-8mm thick. Layer of cement mortar of 1:1 mix (1unit- cement, 1unit- Fine screened sand) in power float finish with proper curing by logging water or sprinkling water or by laying wet gunny bags etc complete as directed. The cost includes Scaffolding all ancillary works as per base builders guidelines and as per site condition . | Sqm | 250 | 795 | 198750
3 | Cement plaster ( To correct External wall undulations) | Providing and applying in one coat, 15mm thick plaster on internal surface of RCC / brick/block walls/ column in cement mortar 1:4, finished rough to take on POP punning. Rate shall include for scaffolding, making grooves, sills, pattas, curing, surface preparation before the application of plaster, providing galvanized chicken mesh to a width of 150 mm at the junctions of masonry and concrete works including tying in position by using suitable nails / clamps / screws and as directed etc. complete at all levels. The contractor shall make good the grooves, pockets etc. after the scaffolding is removed.. Make - Coromandel, L&T, Steel : TATA/ Jindal | Sqm | 100 | 424 | 42400
4 | 150mm thick Aerocon wall - Intermediate wall - Future Exp Area & Handwash, Plate wash,server room,Battery ups room,Cafeteria | Providing & constructing of AAC wall set in adhesive 5mm to 10mm thick / 1:4 cement mortar, inclusive of single coat rough Cement Plaster on both sides of wall in 1:4 , with minimum 2 nos of 6mm dia MS bars (Including tie bars) with 75mm height cement concrete at every 5 courses. Rates to include scaffolding, curing, RCC Lintel, at all heights, constructed to true line & plumb, etc., complete as per the Architect's instructions. Note : Rate should be inclusive of Masking for fixtures & wooden frames. Wall to be built till true ceiling. Rate to include RCC lintel (Lintel overlap length - 300mm to 450mm both ends -length vary based on door size) at necessary heights for doors (Lintel - door bottom & top). Curing of blocks to be done till the satisfactory of PM's. At the junction of RCC structure & block walls, Necessary Wall hacking and cement slurry to be considered on existing structure joints overlap and finished with POP Punning. * Density - 550-700 kg/m3 * Compressive strength - 30 - 50 kg/cm2 * Fire Resistant - Highly fire resistant & able to withstand the standard fire for 240minutes under load. * ISI Mark & Norms - products have ISI (BIS) norms and marking and are conforming to Indian standards. Blocks are conforming to IS 2185 (part 3). * Sound Absorption - Sound absorbency of air borne sound for 3" & 4" walls is 38 to 40 db. Mode of Measurement : Wall will be measured on one side (i.e. Total length of the wall x height of wall {LxH}) | Sqm | 232 | 2597 | 602504
5 | 100mm thick Aerocon wall - AHU Opening closure | Providing & constructing of AAC wall set in adhesive 5mm to 10mm thick / 1:4 cement mortar, inclusive of single coat rough Cement Plaster on both sides of wall in 1:4 , with minimum 2 nos of 6mm dia MS bars (Including tie bars) with 75mm height cement concrete at every 5 courses. Rates to include scaffolding, curing, RCC Lintel, at all heights, constructed to true line & plumb, etc., complete as per the Architect's instructions. Note : Rate should be inclusive of Masking for fixtures & wooden frames. Wall to be built till true ceiling. Rate to include RCC lintel (Lintel overlap length - 300mm to 450mm both ends -length vary based on door size) at necessary heights for doors (Lintel - door bottom & top). Curing of blocks to be done till the satisfactory of PM's. At the junction of RCC structure & block walls, Necessary Wall hacking and cement slurry to be considered on existing structure joints overlap and finished with POP Punning. * Density - 550-700 kg/m3 * Compressive strength - 30 - 50 kg/cm2 * Fire Resistant - Highly fire resistant & able to withstand the standard fire for 240minutes under load. * ISI Mark & Norms - products have ISI (BIS) norms and marking and are conforming to Indian standards. Blocks are conforming to IS 2185 (part 3). * Sound Absorption - Sound absorbency of air borne sound for 3" & 4" walls is 38 to 40 db. Mode of Measurement : Wall will be measured on one side (i.e. Total length of the wall x height of wall {LxH}) | Sqm | 10 | 2491 | 24910
6 | Self Levelling | Providing and laying of Ardex Commercial levelling cementitious flooring system Surface preparation: Removing all existing weak, un sound CC floor to reach the strong substrate, cleaning the floor area to make it free from all contaminants and complete as per manufacturer's specification. Providing and applying Ardex P 51 primer to the base substrate and allow it to dry completely. Providing and mixing of CL 11, commercial levelling compound consisting of high quality special cement and selected fillers, with water at rate of 5.5-6 Ltr for 25 Kg bag of CL 11, installing at required 3mm to 5mm thickness using suitable pin rake trowel and notch trowel, finally rolling the surface with spike roller and allowed to dry completely, installing vinyl /LVT flooring as per client's requirement, etc and complete as per manufacturer's specification. [ The properties shall confirm to:- Bulk density of powder: Approx. 1.3 kg / Ltr; Weight of fresh mortar: Approx. 2.0 kg / Ltr; Working time: Approx. 25 min; Flow life: Approx. 15 min; Initial set (Vicat): Approx. 40 min; Final set (Vicat) Approx. 1 hr; Ball impact hardness: 6.5mm; Scratch hardness: 1.6mm; Compressive strength: 20 N / Up to 3mm thk self levelling) | Sqm | 925 | 477 | 441225
D | PARTITION & PANELLING |  |  |  | 0 | 0 |  | Final Measurement Qty | Amount
1 | Double glazed partition - up to 2400mm - Black color frame -Double glass- Sandwitch Glass | Supply and fixing of Double glazed Partition - GD-105W+ Geze Dela Partition system - Black Anodized: Supply and Fixing of Geze Dela System GD-105W+ i.e., Double glazed modular system consist of Aluminium section of 30x105x1.5mm thick. All sections duly anodised up to 20–25 microns with 6063-T6 grade and required accessories i.e. glass to glass aluminium I/H sections, T section & 90 degree L sections & Glass packing to adjust the floor level. Ceiling profile, Floor profile and wall profile are 30 mm visible face and 105 mm wide with 11.52mm laminated glass + Air Gap + 11.52 mm laminated glass with insertion of Thermoplastic gasket to adhere the glass firm & airtight. Make: GEZE / Eq from JEB / Alloy | Sqm | 104 | 14808.2 | 1540052.8 | Alloy Make considered | 92.18 | 1365019.876
2 | Full Ht. Single Glazed partitions - 2400 mm Height . - - Black colour frame | Supply and installation of full height Single glazed partitions formed out of the following components. Fabricating and Fixing of Glazed Partition with Anodized Aluminium Partition System of 100 x 25/35 mm thick section type placed both horizontally & vertically, Finish of frame : Anodized aluminium with black powder coated as approved by architect. The glazing to be formed out of 10 mm thick toughened glass as per details. The glass to be butt jointed with 2 to 3 mm edge chamfer & edge polishing all around. The butt joint of the glass shall have the aluminium profile & sealed using 3M glass to glass joint tape. Rate to include necessary 12mm thick MDF support finished with approved paint at the junction of false ceiling/solid partition & glass partition as per details .Rate to include 12mm thk MDF strip between modular frame and gypsum partitions all round and finished with paint as per details . Only visible glass surface will be measured and paid for this item. Fixing to be followed as per manufacturers specification. The height of glass partition to be 2.6mtr . Make : GEZE /JEB / Alloy | QRO-Sqm |  | 6148 | 0 | Alloy Make considered
3 | Partition above Glass partition - 100 mm thk (2+2 Layers Gypsum) - Gyproc - 100mm (50mmX25 mm Alu. Box section- 12.5mm thk plain board . Outer skin - 13 mm thk rigiroc Gypsum Board - 2+2 skin ( 100 mm thk) | Providing and fixing baffle partition above glazed partition and doors of overall thickness of 100mm with the following components. The Frame work consist of 25mm x 50mm x 1.2mm thick extruded Aluminium box section framework at spacing not exceeding 600mm both ways (horizontal and vertical). The framework shall be secured at floor, structural ceiling and sill/ Lintel level. Framework to be secured to Floor / Walls / Columns / Ceiling / Beams using 75mm metal screws and dowels as per details.The framework to be cladded inner layer 12.5 mm thk plain Gypsum board & Outer layer of 13mm thick RIGIROC Gypboard, conforming to IS 2095 Part 1:2011, having flexural strength – {Longitudinal > 500N & transverse > 180N} on either side of the framing on either side of the framing from False ceiling level up to true ceiling level in line and level screw fixed with 25mm & 35mm drywall screws at 300mm centre to centre (150mm C/C at Floor & True Ceiling level) with staggered joints to avoid through joints. The board shall be jointed and finished to have a flushed look by filling and finishing with proprietary supplied jointing tape & compound and Two coats of Dry wall coat as per manufacturer's specification. Joints to be sand papered to achieve a smooth and seamless finish as per architects approval. Gypsum surface to be fully treated and finished to receive the Paint . Includes Putty , Primer etc., As an acoustic requirement, the cavity between the Boards shall be placed with 50mm thick Rock wool of density 48kg/m3, blanket wrapped in RP tissue suitably affixed to partition framework using where necessary GI binding wire, duct tape as indicated in the drawing. Note : Rock Wool with RP.Tissue packing of size 600 x 600mm/ 1200X600 mm . The junction of the partition with masonry & all penetration through the partition has to be treated with Hilti CP 606/ Hilti CP 620 / Pyroplex 2WT3IOP fire and acoustic sealant. Note : Aluminium section / plywood support to be provided wherever required for extra support to fix aluminium skirting, doors, storages, writing boards, glass boards, soft boards, projection screens, LED, paintings, artifacts, display, light fixtures, niches, glazed partition, mirrors, reader panel as per architects instructions. Meeting rooms with LED mounts to have sufficient aluminium & plywood support to house the bracket / mount. The partition cost should include Borer / Antitermite treatment for salwood and plywood as per architects instructions and dwg. Also cost to include making cut outs for AC ducts / Electrical works / Security systems / other services works / Switches / Sockets etc., complete. Wherever required by contractors and on completion of ducting, wiring work, the opening / cutouts to be closed as not to allow any transmission of sound or air as per architect's / PM's instructions. Partition installation to be done as per Gyproc/USG standard Installation process . One 4 pax meeting room full mock up to be done and approved by gyproc/USG Technical team /PM/ Architect . | Sqm | 108.8 | 4108.3639 | 446989.9932
4 | 100 mm thk Double Skin Gypsum partition - Make: Gyproc - Inner skin - 12.5mm thk plain board . Outer skin - 13 mm thk rigiroc Gypsum Board - 2+2 skin ( 100 mm thk) | Providing and fixing 100 mm thk double skin gypsum partition - FRAME WORK: To be formed of cold rolled GI studs of size 48mm (0.5mm thk having one flange of 34mm and another flange of 36mm made of GI Steel), placed at 600mm centre to centre fixed onto the floor channels. The GI channels of size 50mm x 0.55mm (section thick) to be fixed on the floor to hold GI studs as per details. Also to have an additional 19mm thick ply supports /rigid salwood frame (wherever required) as spacer at the false ceiling level and as sub frames for doors and glazed openings as per details or as per architects instruction. INSULATION: As an acoustic requirement, contractor to affix 50mm thick Rock Wool of density 48 kg/m3 wrapped in RP tissues suitably affixed to partition framework using necessary GI binding wire, duct tape as indicated in the drawing. CLADDING: The inner layer to be finished with 12.5 mm thk tapered edge gypsum board (IS-2095 Part 1:2011) and the outer layer 13mm thk RIGIROC Gypsum board (from Finished floor level to till false ceiling) of in line and level screw fixed with 25mm drywall flat head screws @ 300mm c/c with staggered joints to avoid through joints and finished with proprietary supplied jointing tape and compound as per manufacturer's specification. Joints to be sand papered to achieve a smooth and seamless finish. Care must be taken that the plasterboards are raised 3mm from the floor and in this gap, chauking compound is injected, for successive layers and similarly for the ceiling channel/sections. Gypsum partition to be installed as per manufacturer specifications.To have 12mm ply to receive the skirting but Rate NOT to include skirting. The junction between partition & ceiling to be provided with 'L' shaped channel as per details. Finishes: Gypsum surface till the false ceiling on both sides - 2 coats of primer to be applied onto the gypsum surface. Surface to be smoothened using chalk putty as directed. Surfaces are then sandpapered to achieve a smooth surface and primer to be applied to receive paint . Make: GYPROC/USG . Note : Rock Wool with RP.Tissue packing of size 600 x 600mm / 600X1200 mm . The junction of the partition with masonry & all penetration through the partition has to be treated with Hilti CP 606/ Hilti CP 620 / Pyroplex 2WT3IOP fire and acoustic sealant. Gypsum surface to be fully treated and finished to receive the Paint . Includes Putty , Primer etc., Note : Aluminium section / plywood support to be provided wherever required for extra support to fix aluminium skirting, doors, storages, writing boards, glass boards, soft boards, projection screens, LED, LED, paintings, artifacts, display, light fixtures, niches, glazed partition, mirrors, reader panel as per architects instructions. Meeting rooms with LED mounts to have sufficient aluminium & plywood support to house the bracket / mount. The partition cost should include Borer / Ant termite treatment for salwood and plywood as per architects instructions and dwg. Also cost to include making cut outs for AC ducts / Electrical works / Security systems / other services works / Switches / Sockets etc., complete. Wherever required by contractors and on completion of ducting, wiring work, the opening / cut-outs to be closed as not to allow any transmission of sound or air as per architect's / PM's instructions. Partition installation to be done as per USG/ Gyproc standard Installation process . One mock up to be done and approved by gyproc/USG Technical team /PM/ Architect . Gypsum surface to be fully treated and finished to receive the Paint . One 4 pax meeting room full mock up to be done and approved by gyproc/USG Technical team /PM/ Architect . | Sqm | 280 | 3720.2012 | 1041656.3225
5 | Single Skin Gypsum partition - Store room - Plain Gypsum Board - 75mm thk (1+1) | Providing and fixing 75 mm thk single skin gypsum partition - FRAME WORK: To be formed of cold rolled GI studs of size 48mm (0.5mm thk having one flange of 34mm and another flange of 36mm made of GI Steel), placed at 600mm centre to centre fixed onto the floor channels. The GI channels of size 50mm x 0.55mm (section thick) to be fixed on the floor to hold GI studs as per details. Also to have an additional 19mm thick ply supports /rigid salwood frame (wherever required) as spacer at the false ceiling level and as sub frames for doors and glazed openings as per details or as per architects instruction. INSULATION:As an acoustic requirement, contractor to affix 50mm thick glass wool of density 48kg/m3 wrapped in RP tissues suitably affixed to partition framework using necessary GI binding wire, duct tape as indicated in the drawing.. CLADDING: The framework to be cladded on both sides with single layer (from Finished floor level to till false ceiling) of 12.5 mm thk tapered edge gypsum board (IS-2095 Part 1:2011) in line and level screw fixed with 25mm drywall flat head screws @ 300mm c/c with staggered joints to avoid through joints and finished with proprietary supplied jointing tape and compound as per manufacturer's specification. Joints to be sand papered to achieve a smooth and seamless finish. Care must be taken that the plasterboards are raised 3mm from the floor and in this gap, chauking compound is injected, for successive layers and similarly for the ceiling channel/sections. Gypsum partition to be installed as per manufacturer specifications.To have 12mm ply to receive the skirting but Rate NOT to include skirting. The junction between partition & ceiling to be provided with 'L' shaped channel as per details. FInishes: Gypsum surface till the false ceiling on both sides - 2 coats of primer to be applied onto the gypsum surface. Surface to be smoothened using chalk putty as directed. Surfaces are then sandpapered to achieve a smooth surface and cost to include 3 coats of Plastic emulsion Paint of approved shade to be applied. Make: GYPROC / USG . Note : Glass Wool with RP.Tissue packing of size 600 x 600mm. The junction of the partition with masonry & all penetration through the partition has to be treated with Hilti CP 606/Pyroplex 2WT3IOP fire and acoustic sealant. Note : Aluminium section / plywood support to be provided wherever required for extra support to fix aluminum skirting, doors, storages, writing boards, glass boards, soft boards, projection screens, LCD, Plasma, paintings, artifacts, display, light fixtures, niches, glazed partition, mirrors, reader panel as per architects instructions. Meeting rooms with LCD mounts to have sufficient aluminium & plywood support to house the bracket / mount. The partition cost should include Borer / Antitermite treatment for salwood and plywood as per architects instructions and dwg. Also cost to include making cut outs for AC ducts / Electrical works / Security systems / other services works / Switches / Sockets etc., complete. Wherever required by contractors and on completion of ducting, wiring work, the opening / cutouts to be closed as not to allow any transmission of sound or air as per architect's / PM's instructions. | Sqm | 25 | 2161.3888 | 54034.7203
6 | Fire rated Gypsum partition ( Server , UPS and Battery Room) | 122mm thick - C-stud partition which includes double layer of tapered edge 12.5mm thick - Fireline of size 1219x2438mm is screw fixed to C-stud. 70x0.5mm C-stud placed at 610mm c/c in 72x0.5mm Floor and Ceiling channel. Floor & Ceiling channel is anchored to the floor & true ceiling using - Rawl plug Ø8x45mm /Hilti X-GN20MX anchor fasteners at 600mm c/c in zig zag manner. Floor channel to be wrapped with 70μ Self Adhesive LDPE moisture barrier film to further improve corrosion resistance performance. 12.5mm thick - Fireline board strip of 72mm width is placed between ceiling channel and RCC ceiling slab when deflection is more than 10mm & fire rating is more than 30min. Noggin channel of 70x0.5mm width has to be provided at the horizontal joints of the two boards. First layer of - boards to be screw fixed with - Drywall screws of 25mm at minimum spacing of 600mm at centre and 600mm at periphery. Second layer to be screw fixed - Drywall screws of 35mm at minimum spacing of 300mm at centre and 300mm at periphery. 50mm glasswool slab of density 24kg/m³ shall be placed in metal framework. Glasswool holding clip should be used to hold glasswool slab in its position. Finally square and tapered edges of the boards are to be jointed and finished so as to have a flush look which includes filling and finishing with - Pro-Fill Jointing compound, - Joint Paper tape or fibre tape. The junction of the partition with masonry & all penetration through the partition has to be treated with Hilti/Pyroplex fire and acoustic sealant. All other detailing and specifications to be followed as per approved shop drawing. Cost Includes 12mm thk bison board backing inside server room to mount Power panels and Distribution boards. The junction of the partition with masonry & all penetration through the partition has to be treated with Hilti CP 606/Pyroplex 2WT3IOP fire and acoustic sealant. Make- Gyproc/ USG - 2 Hr fire line board and sections . All detailing and specifications to be followed as per approved drawing of Gyproc. Contractors should strictly adehre manufacturers guidelines for installation . After completion of work , Manufacturers technical team to inspect the installation and provide certificate for 2HR fire rating . Make: GYPROC / Eq. USG | Sqm | 10 | 4134.2414 | 41342.4143
7 | Aluminium frame work - 50X50 mm - Only Frame work | Providing and fixing partitions consisting of 50mm x 25mm x 1.2mm Aluminum sections framework with all necessary reinforcements required of wood/aluminum, at spacing not exceeding 600mm bothways. ( horizontal & vertical) Partition framework to be provided with bracing/angular supports & secured to structural ceiling & nearest structural member using 75mm galvanized metal screws & wooden dowels. Cost to include provision of cut outs for duct and cable tray routing above ceiling at locations indicated on the drawings or as instructed by the architects. | Sqm | 25 | 1296.9565 | 32423.9128 | Aluminium frame work - 50X25 mm as per the query response.
8 | Aluminium frame work - 25X25 mm - Only Frame work | Providing and fixing partitions consisting of 25mm x 25mm x 1.2mm Aluminum sections framework with all necessary reinforcements required of wood/aluminum, at spacing not exceeding 600mm bothways. ( horizontal & vertical) Partition framework to be provided with bracing/angular supports & secured to structural ceiling & nearest structural member using 75mm galvanized metal screws & wooden dowels. Cost to include provision of cut outs for duct and cable tray routing above ceiling at locations indicated on the drawings or as instructed by the architects. | Sqm | 10 | 1102.8751 | 11028.7513
9 | One skin Gypsum on Aluminium/ GI frame work | Installaing one skin gypsum board on Aluminium / GI frame work . Only Gypsum board supply and installation cost to be quoted (Excluding Frame work) | Sqm | 10 | 410.6516 | 4106.5155
10 | Two skins Gypsum on Aluminium/ GI frame work | Installaing two skins gypsum board on Aluminium / GI frame work . Only Gypsum board supply and installation cost to be quoted (Excluding Frame work) | Sqm | 10 | 821.3031 | 8213.031
0
E | DOORS |  |  |  | 0
1 | 1050x 2600 mm Aluminium Door Frame & Style Shutter - Double Glazed Stile Shutter Door(Cabin and Conference) | Door Jamb : 100mm X 25mm Proprietary anodised aluminium section with anodised finish Action : Single Swing . 100X25X2600 mm Ht . Door frame to be grouted to the PCC Floor with suitable Brackets as per manufacturers specification. Door vertical frame to be fixed to the adjucent gypsum partition with suitable Ply backing as per manufacturers guidelines . Shutter Construction : 6mm +6 mm Double glazed Toughened Glass with 70 mm x 45mm anodized aluminium frame stile shutter of size 1050mm X 2600mm Hinge Type : 5 Nos Hinges . Dorma / Geze 5" Flush suitable to style shutte Lockset : Dorma 952 Narrow style lock / GEZE 8134002 Door Handle : D Type offset handle 450 mm high Door Closer: - Dorma TS 91 cam action Door Closer with hold-open slide arm / GEZE TS 3000 V; Door Stopper : Dorma / Geze Seals: Drop down sealsSecurity system: provide provision for magnetic access control. Door frame make: Alloy / Geze / JEB Glass- Saint Gobain . | Nos | 2 | 98050 | 196100 | Door Frame - Alloy make considered Hardware - Gaze make considered | 2 | 196100
2 | 1200x 2550 mm Aluminium Door Frame & Style Shutter | Door Jamb : 100 /105 mm X 25 mm Proprietary anodised aluminium section with black powder coated finish.. Black anodised . Action : Single Swing . 100X25X2550 mm Ht . Door frame to be grouted to the PCC Floor with suitable Brackets as per manufacturers specification. Door vertical frame to be fixed to the adjacent gypsum partition with suitable Ply backing as per manufacturers guidelines . Black anodised Shutter Construction : 10mm thick Toughened Glass with 70 mm x 45mm anodized aluminium frame stile shutter of size 1200mm X 2550mm . Black anodised Hinge Type : 5 Nos Hinges . Dorma / Gaze 5" Flush suitable to style shutter Lockset : Dorma 952 Narrow style lock / GEZE 8134002 Door Handle : D Type offset handle 450 mm high . Black anodised Door Closer: - Dorma TS 91 cam action Door Closer with hold-open slide arm / GEZE TS 3000 V; Black anodised Door Stopper : Geze / Dorma Seals: Drop down seals Dorma / Geze - Gap b.w finished floor and Door shutter should not exceed 4mm . Security system: provide provision for magnetic access control. Door frame and shutter make: GEZE / Alloy / JEB .. Glass- Saint Gobain . . Note: Individual measurements to be taken for all doors and shop dwg to be submitted for approval . One Mock up to be done with all hardwares with in 7 days from the project start date . | Nos | 1 | 59667.4 | 59667.4 | Door Frame - Alloy make considered Hardware - Gaze make considered | 1 | 59667.4
3 | 1050x 2550 mm Aluminium Door Frame & Style Shutter | Door Jamb : 100mm X 25mm Proprietary anodised aluminium section with black powder coated finish.. Black anodised Action : Single Swing . 100X25X2550 mm Ht . Door frame to be grouted to the PCC Floor with suitable Brackets as per manufacturers specification. Door vertical frame to be fixed to the adjacent gypsum partition with suitable Ply backing as per manufacturers guidelines . Black anodised Shutter Construction : 10mm thick Toughened Glass with 70 mm x 45mm anodized aluminium frame stile shutter of size 1050mm X 2550mm . Black anodised Hinge Type : 5 Nos Hinges . Dorma / Gaze 5" Flush suitable to style shutter Lockset : Dorma 952 Narrow style lock / GEZE 8134002 Door Handle : D Type offset handle 450 mm high . Black anodised Door Closer: - Dorma TS 91 cam action Door Closer with hold-open slide arm / GEZE TS 3000 V; Black anodised Door Stopper : Geze / Dorma Seals: Drop down seals Security system: provide provision for magnetic access control. Door frame and shutter make: GEZE / Alloy / JEB .. Glass- Saint Gobain . | Nos | 8 | 58607.4 | 468859.2 | Door Frame - Alloy make considered Hardware - Gaze make considered | 8 | 468859.2
4 | 900x 2550 mm Aluminium Door Frame & Style Shutter | Door Jamb : 100mm X 25mm Proprietary anodised aluminium section with black powder coated finish.. Black anodised Action : Single Swing . 100X25X2550 mm Ht . Door frame to be grouted to the PCC Floor with suitable Brackets as per manufacturers specification. Door vertical frame to be fixed to the adjacent gypsum partition with suitable Ply backing as per manufacturers guidelines . Black anodised Shutter Construction : 10mm thick Toughened Glass with 70 mm x 45mm anodized aluminium frame stile shutter of size 900mm X 2550mm . Black anodised Hinge Type : 5 Nos Hinges . Dorma / Gaze 5" Flush suitable to style shutter Lockset : Dorma 952 Narrow style lock / GEZE 8134002 Door Handle : D Type offset handle 450 mm high . Black anodised Door Closer: - Dorma TS 91 cam action Door Closer with hold-open slide arm / GEZE TS 3000 V; Black anodised Door Stopper : Geze / Dorma Seals: Drop down seals Security system: provide provision for magnetic access control. Door frame and shutter make: GEZE / Alloy / JEB .. Glass- Saint Gobain . | Nos | 2 | 58607.4 | 117214.8 | Door Frame - Alloy make considered Hardware - Gaze make considered | 3 | 175822.2
5 | 900 x 2550 mm Aluminium Door Frame & Flush door with Full Ht (Store room-01,02 and IT Store) | Door Jamb : 100mm X 25mm Proprietary anodised aluminium section with black powder coated finish.. Black anodised Action : Single Swing . 100X25X2550 mm Ht . Door frame to be grouted to the PCC Floor with suitable Brackets as per manufacturers specification. Door vertical frame to be fixed to the adjacent gypsum partition with suitable Ply backing as per manufacturers guidelines . Black anodised Shutter Construction : 32mm thk Flush door in laminate finish with vision panel as per detail dwg Hinge Type : 4 Nos Hinges . Dorma / Gaze 5" Flush suitable to style shutter Lockset : Dorma 952 Narrow style lock / GEZE 8134002 Door Handle : D Type offset handle 450 mm high . Black anodised Door Closer: - Dorma TS 71 Door Closer / Eq GEZE Door Stopper : NA Vision panel : 300 x200mm Security system: provide provision for magnetic access control. Door frame and shutter make: GEZE / Alloy / JEB .. Glass- Saint Gobain . | Nos | 3 | 49979 | 149937 | Door Frame - Alloy make considered Hardware - Gaze make considered | 2 | 99958
6 | 750 x 2550 mm Aluminium Door Frame & Flush door with Full Ht | Door Jamb : 100mm X 25mm Proprietary anodised aluminium section with black powder coated finish.. Black anodised Action : Single Swing . 100X25X2550 mm Ht . Door frame to be grouted to the PCC Floor with suitable Brackets as per manufacturers specification. Door vertical frame to be fixed to the adjacent gypsum partition with suitable Ply backing as per manufacturers guidelines . Black anodised Shutter Construction : 32mm thk Flush door in laminate finish with vision panel as per detail dwg Hinge Type : 4 Nos Hinges . Dorma / Gaze 5" Flush suitable to style shutter Lockset : Dorma 952 Narrow style lock / GEZE 8134002 Door Handle : D Type offset handle 450 mm high . Black anodised Door Closer: - Dorma TS 71 Door Closer / Eq GEZE Door Stopper : NA Vision panel : 300 x200mm Security system: provide provision for magnetic access control. Door frame and shutter make: GEZE / Alloy / JEB .. Glass- Saint Gobain . | Nos | 1 | 49979 | 49979 | Door Frame - Alloy make considered Hardware - Gaze make considered | 1 | 49979
7 | FRD - 1200x 2400mm (Server /UPS ) | Providing and fixing of 2 Hr Fire rated metal door Single shutter made of 1.6mm thk galvanized steel frames of size 140x57 mm with rebate and 1.2mm thk galvanized steel of 46mm thk double skin shutter with necessary infill materials and glue/sealant fixed in all respect including poly urethane paint with protective film coating and all accessories like hinges, lock, handles, door closers, with 6mm thk Toughened fire glass vision panel (without mesh) etc., as per the specifications. (Make - Dorma) (Note - Before ordering Cross Check the site for Dimension & get the approval from the architect with shop drawing) Make : RNB / Shakthi /HADID . make: Door Closer - Dorma TS 91 cam action Door Closer with hold-open slide arm / GEZE TS 3000 V; Handle: Dorma / Geze - 450 mm High "D" type Handle; Hinges - Dorma / Geze suitable to 2HR fire door ; | Nos | 2 | 57240 | 114480 | Shakthi Make considered |  | 0
8 | FRD - 1050x 2100mm ( Battery room) | Providing and fixing of 2 Hr Fire rated metal door Single shutter made of 1.6mm thk galvanized steel frames of size 140x57 mm with rebate and 1.2mm thk galvanized steel of 46mm thk double skin shutter with necessary infill materials and glue/sealant fixed in all respect including poly urethane paint with protective film coating and all accessories like hinges, lock, handles, door closers, with 6mm thk Toughened fire glass vision panel (without mesh) etc., as per the specifications. (Make - Dorma) (Note - Before ordering Cross Check the site for Dimension & get the approval from the architect with shop drawing) Make : RNB / Shakthi/ HADID . make: Door Closer - Dorma TS 91 cam action Door Closer with hold-open slide arm / GEZE TS 3000 V; Handle: Dorma / Geze - 450 mm High "D" type Handle; Hinges - Dorma / Geze suitable to 2HR fire door ; | Nos | 1 | 55120 | 55120 | Shakthi Make considered |  | 0
9 | FRD - 1000x 2400mm ( Fire exit) | Providing and fixing of 2 Hr Fire rated metal door Single shutter made of 1.6mm thk galvanized steel frames of size 140x57 mm with rebate and 1.2mm thk galvanized steel of 46mm thk double skin shutter with necessary infill materials and glue/sealant fixed in all respect including poly urethane paint with protective film coating and all accessories like hinges, lock, handles, door closers, with 6mm thk Toughened fire glass vision panel (without mesh) etc., as per the specifications. (Make - Dorma) (Note - Before ordering Cross Check the site for Dimension & get the approval from the architect with shop drawing) Make : RNB / Shakthi/HADID . make: Door Closer - Dorma TS 91 cam action Door Closer with hold-open slide arm / GEZE TS 3000 V; Handle: Dorma / Geze - 450 mm High "D" type Handle; Hinges - Dorma / Geze suitable to 2HR fire door ; | Nos | 1 | 55120 | 55120 | Shakthi Make considered |  | 0
10 | Aluminium profile Boxing | Providing and fixing 0f 200 X100/105 mm Aluminium boxing to install access reader / switches as per manufacturers specification. Boxing to be installed adjacent to door frame as per detail design . Make: GEZE /JEB /Alloy | Nos | 12 | 21681.8182 | 260181.8182 | Alloy Make considered | 14 | 303545.4545
11 | Firerated shaft shutters | Replacing of existing Laminate shutters with fire-rated shutters. | Nos | 4 | 16430 | 65720 | Size: 1200 X1200MM (As per the query response)
12 | Reception Main Entry door - 2 HR FIRE RATED GLASS DOOR _ SAINTGOBAIN | Providing and fixing of tested fully glazed steel fire rated double leaf door with 120 minutes of integrity and radiation control and partial insulation (EW=120 and EI=20) with symmetrical (Bi-Directional) fire protection. The system shall be tested as per EN 1634-1 standard in an accredited international laboratory. The glass shall be CONTRAFLAM LITE (14mm) clear, non-wired, toughened, interlayered, 120 minutes fire-rated glass for integrity and radiation control (EW 120) and insulation (I 20) with a light transmission of 86% and a sound reduction of 38 dB and manufactured in UL & TUV audited facility and including UL-EU Certification and compliant to class 1(B)1 category of Impact Resistance as per EN 12600. The glass shall be tested for 5000 hours of UV resistance as per EN ISO 12543-4. The glass shall be EPD (Environmental Production Declaration) verified in accordance to EN 15804 and ISO 14025 in which its life cycle assessment is performed considering Cradle to Gate system boundaries. The glass must produce a recycled content declaration committing to a pre-consumer cullet of up to 11% and post-consumer cullet less than 1%. The glass shall provide bi-directional (symmetrical) fire protection. The door frames are manufactured from 1.6 mm galvanized steel sheet pressed to form a profile of 35 mm x 60 mm on the vertical sides and 50 x 60 mm on the horizontal side. The door shutter would have a top rail and side rail 60 mm x 60 mm and a bottom rail of 110 mm x 60 mm. The glass should be held in its place with the help of 1.6 mm GI beading and a special ceramic tape with cross section of 5 x 20 mm as per the test evidence. Beading should be attached using 4 mm x 35 mm SS screws at a distance of 75 mm from the edges and 150 mm c/c henceforth. The shutters should be fixed to the frame using Dorma SS Ball Bearing Hinges of size 100 mm x 89 mm and 3 mm thickness or equivalent. The door should be fitted with necessary hardware including TS 3000V or TS 73V, lock, 900mm offset handle and tower bolt from Dorma / Geze / equivalent. The test report will be considered valid only if it contains the stamp and signature of the authorized signatory from Saint-Gobain Glass India Ltd |  |  | 0 | 0 | Fire Rated Glass - Vetrotech Saint-Gobain make considered. Hardware - Gaze make considered.
A | Size - 2000 X2400 mm | Door size- 2000 X 2600 mm ( Double Shutter) | Nos | 1 | 432533.9815 | 432533.9815 |  | 1 | 432533.9815
B | Size - 1200 X2400 mm | Door size- 1200 X 2600 mm ( Single Shutter) | QRO-Nos |  | 268183.18 | 0
13 | 120 MINUTES FULLY GLAZED VDS® FIRE RESISTANT FIXED NON LOAD BEARING PARTITION | 120 MINUTES FULLY GLAZED VDS® FIRE RESISTANT FIXED NON LOAD BEARING PARTITION SYSTEM PROVIDING INTEGRITY AND RADIATION CONTROL (EW) Supply and installation of tested Vetrotech Saint-Gobain VDS® fully glazed fire rated fixed partition with 120 minutes of integrity and radiation control (EW 120) with symmetrical (bi-directional) fire protection. The frames shall be made with imported cold rolled profiles. The frames are cold rolled from 1.5 mm steel sheet to form a profile of 50 mm x 50 mm on all sides. The system shall be tested as per EN 1364-1 in an international accredited laboratory. The glass should be CONTRAFLAM LITE (14mm) clear, non-wired, toughened, interlayered, 120 minutes fire-rated glass for integrity and radiation control (EW 120) and insulation (I 20) with a light transmission of 86% and a sound reduction of 38 dB and manufactured in UL & TUV audited facility and including UL-EU Certification (File number R38101) and compliant to class 1(B)1 category of Impact Resistance as per EN 12600. The glass shall be tested for 5000 hours of UV resistance as per EN ISO 12543-4. The glass shall be EPD (Environmental Production Declaration) verified in accordance to EN 15804 and ISO 14025 in which its life cycle assessment is performed considering Cradle to Gate system boundaries. The glass must produce a recycled content declaration committing to a pre-consumer cullet of up to 11% and post-consumer cullet less than 1%. The glass shall provide bi-directional (symmetrical) fire protection. The glass should be held in its place with the help of 1.5 mm cold rolled steel beading and Kerafix 2000 ceramic tape with cross section of 4 x 15 mm as per the test evidence. The beading shall be clipped on using stainless steel self-tapping screws fixed at a distance of 70 mm from the edges and 150 mm c/c henceforth. The glass panes are to be supported on noncombustible 6 mm thick calcium silicate setting blocks. The maximum glazing size shall be as per the test certification. The profile has to be fixed to the supporting construction by means of M10 or bigger steel bolts at every 150 mm from the edges and every 500 mm (approx.) c/c. The partitions shall offer C4 level of wind resistance when tested as per EN12211 and shall provide class 4 level of air permeability as per EN 1026. The partitions shall also be tested for class 5 of impact resistance when tested as per EN 13049. The partitions shall also be tested for class 4 level of mechanical strength when tested as per EN13115. The partitions shall have water tightness level of 8A when tested as per EN 1027. Test evidence: The test report will be considered valid only if it contains the stamp and signature of the authorized signatory from Vetrotech Saint-Gobain. | QRO-Nos |  | 64185.12 | 0 | Fire Rated Glass - Vetrotech Saint-Gobain make considered. Hardware - Gaze make considered.
F | CEILING WORKS |  |  |  | 0
1 | Modular false ceiling - 0.5/0.6 NRC ( Store rooms , Server, UPS , Battery , BMS ) | Providing and fixing in true horizontal level modular false ceiling using hot dipped galvanised steel sections. Exposed surface chemically cleaned capping prefinished in baked polyester paint. Shallotte/ Black Reveal grids and approved Shadow line wall angle of size 3000mmx19mmx19mm used in the periphery of the ceiling fixed to the partition, R.C.C.columnand walls using screws at 600mm c/c. Main runner of size15mmx32mmx3000mm suspended at 1200 c/c, using 2mm/3mm dia.GI butterfly wire hanger safely fixed to the structural soffit of the RCC slab using 6mm anchor fastener at every 1200mm c/c (max.) and 1200mm long cross tee of size 15mmx27mmx1200mm to be interlocked between main runner at 600mm c/c (max.) to form a grid of 600mx600mm. Tile to have 0.55 / .6 NRC sound. Tile sample to be approved by ARCHITECT WHILE quoting. Make - Armstrong- Dune max / Eq in Daiken . | Sqm | 60 | 1643 | 98580
2 | Modular false ceiling - 0.9 NRC | Providing and fixing in true horizontal level modular false ceiling using hot dipped galvanised steel sections. Exposed surface chemically cleaned capping prefinished in baked polyester paint. Shallotte/ Black Reveal grids and approved Shadow line wall angle of size 3000mmx19mmx19mm used in the periphery of the ceiling fixed to the partition, R.C.C.columnand walls using screws at 600mm c/c. Main runner of size15mmx32mmx3000mm suspended at 1200 c/c, using 2mm/3mm dia.GI butterfly wire hanger safely fixed to the structural soffit of the RCC slab using 6mm anchor fastener at every 1200mm c/c (max.) and 1200mm long cross tee of size 15mmx27mmx1200mm to be interlocked between main runner at 600mm c/c (max.) to form a grid of 600mx600mm. Tile to have .9 NRC sound. Tile sample to be approved by ARCHITECT WHILE quoting. Make - Armstrong- 0.9 NRC - Mineral Fibre Tile - Sample to be submitted for Approval | Sqm | 380 | 1961 | 745180
3 | Metal grid ceiling(Handwash and plate wash) | Providing and fixing 600X600 mm Aluminium perforated false ceiling using 24 mm GI & steel grid . Basic Price -1800 / sqm Nextior / Armstrong / Fameline | Sqm | 45 | 2301.048 | 103547.16
4 | Gypsum false ceiling | Providing and fixing Gypsum False Ceiling which includes G.I.Perimeter Channels of size .55mm thick (having One Flange of 20mm. and another flange of 30mm and a web of 27mm) along with perimeter of ceiling, screw fixed to brick wall / partition with the help of Nylon sleeves and screws at 610mm centres. Then suspending G.I. intermediate channels of size 45mm (0.9mm thick with 2 flanges of 15mm each) from the soffit at 1220mm centres with ceiling angle of width 25mm X 10mm X 0.55mm thick fixed to soffit with G.I. cleat and steel expansion fasteners. Ceiling section of 0.55mm thick having knurled web of 51.5mm and 2 flanges of 26mm each with lips of 10.5mm are then fixed to the intermediate channel with the help of connecting clips and in direction perpendicular to the intermediate channel at 450 mm centres Cost inclusive of one coat of primer and 3 coats of emulsion paint. Make of Stud & Channel - Gyproc /USG . Make of gypsum - Gyproc/USG . Installation to be done as per manufacturers installation guidelines . Cost includes 150 mm high vertical band and cove light provision. | Sqm | 400 | 1272 | 508800
5 | Gyp false ceiling for Open ceiling area - (to be fixed at True ceiling to achieve smooth finish) | Providing and fixing Gypsum False Ceiling which includes 12.5 mm thk gypsum board , GI Ceiling section to be fixed to the true ceiling with suitable frame work. sections to be fixed at 600 mm c/c centre as per dwg . Cost inclusive of providing scaffolding for open office ceiling and one coat of primer and 3 coats of approved emulsion paint. Note : Marking of Electrical, Fire Alarm & Air-conditioning & co-ordination with marking of fixtures to be considered. Necessary cut-outs shall be provided for taking of light cables, Fire and safety cables which shall be neatly finished after fixing of equipment's thereby leaving no gaps, etc., complete Measurement to be along the horizontal surface of the ceiling Make Frames : Gyproc /USG ; make Gypsum - Gyproc /USG | Sqm | 50 | 1272 | 63600
6 | Knauf - Danoline- Random perforation ceiling | Providing and fixing suspended false ceiling-Knauf Danoline - Strato panel random dia perforated G8/15/20 of size 600x600x12.5mm: Regular round perforation which includes providing and fixing GI perimeter channels of size 0.55 mm. Thk. having one flange of 20 mm and another flange of 30 mm and web of 27 mm along the perimeter of the ceiling, screw fixed to brick wall/ partition with help of nylon sleeves and screws, at 610 mm centers. The suspended GI intermediate channels of size 45 mm,0.9mm thk with two flanges of 15 mm each from the soffit at 900 mm centers with ceiling angle of width 25mm x 10mm x 0.55mm thk fixed to soffit with GI cleat and steel expansion fasteners. Ceiling section of 0.55 mm thk fixed to the intermediate channels with help of connecting clips and in direction perpendicular to the intermediate channel with centers of 333 mm perforated gypboard is then screw fixed to ceiling section with 25 mm dry wall screws at 300 mm centers. Screw fixing is done mechanically either with screw driver or drilling machine with suitable attachment. (Cost to be quoted inclusive of wastages- Pl refer Dwg) . Make- Knauf | Sqm | 40 | 3021 | 120840
7 | Axiom Trim | Providing & fixing 100mm wide axiom - extruded aluminium trim in curved length, finished powder coated in approved shade, installed complete with connector clips and C/C grid suspension distance all as per manufacturer's specifications. Make - USG, Arm strong, Daiken, Fameline | Rmt | 25 | 583 | 14575
8 | Baffle ceiling - Made of 12mm thk Eco board |  |  |  | 0
| Huddle Space - Plain Eco board | 12mm thk , 150 mm High Eco board baffle ceiling , c/c gap 100 mm to be suspended from Gypsum ceiling / True ceiling with suitable frame support . Cost includes necessary black color GI frame support and ply backing on Gypsum ceiling to hold the frame work . | Sqm | 5 | 12076.1747 | 60380.8733 | Basic price Rs.980/Sft considered as per the query response.
| Huddle Space - Printed Eco board | 12mm thk , 200 mm High Printed Eco board baffle ceiling , c/c gap 100 mm to be suspended from Gypsum ceiling / True ceiling with suitable frame support . Cost includes necessary black color GI frame support and ply backing on Gypsum ceiling to hold the frame work . | Sqm | 25 | 12076.1747 | 301904.3664 | Basic price Rs.980/Sft considered as per the query response.
| Café - Printed Eco board | 12mm thk , 300 mm High Printed Eco board baffle ceiling , c/c gap 100 mm to be suspended from Gypsum ceiling / True ceiling with suitable frame support . Cost includes necessary black color GI frame support and ply backing on Gypsum ceiling to hold the frame work . | Sqm | 50 | 12076.1747 | 603808.7328 | Basic price Rs.980/Sft considered as per the query response.
9 | Extruded Aluminium Baffle Ceilings of size 25mm (Base) x 100mm (Height) x 1 mm (Thickness) - Wood Finish -Reception | Supply and Installation of Baffle ceilings of size 100mm(Height) x Size 25mm(Base) x 1mm thick extruded aluminium 6063AA in Architect approved Wood Grain Finish suspended to a Multi-slotted baffle C Carrier made of 0.8mm thick Galvanised steel surface finished in Black colour powder Coated finish. The baffle is connected the Baffle Carrier at a centre to centre distance of 100 mm with a bolt/nut/Spring washer arrangement as per typical detail attached. The baffle C Carrier is suspended from the RCC True Ceiling at every 1m in general and at 150mm from Baffle Joints using an M6 Threaded Rod and suitable anchor fastener. The baffles come at a maximum size up to 6 m in length. The baffle end with an End Cap made in Aluminium and is with same finish as the baffle panel. Two baffle are connected by splice to make it run continuously or with a Gap of 20mm as per architect’s approval. The rate quoted for false ceiling system shall include providing necessary cut-outs/supports for all fixing light fixtures (all sizes) AC diffuser, AC dampers, AC linear grills, smoke detectors, speakers, etc. and any other openings to be made in false ceiling as directed. . Make: Armstrong / Hunter Douglas /Frameline / Nextior | Sqm | 50 | 6777.445 | 338872.248 | Fameline make considered.
10 | Metal Ceiling (Triangular Aluminium cell ceiling) | Providing and fixing of triangle patent ceiling with tiles made of .8 mm thk, 60 mm height aluminium with clip in system. Above ceiling services (ducts, tray, conduits) and true ceiling to be finished in black colour. Make: Frameline | sqm | 80 | 5175.5034 | 414040.2739 | Fameline make considered. Aluminium Triangle cell ceilings with Cell ceilings sections A, B and C of size 25 mm (base) x 100 mm( Height) x 2500 mm ( Length ) , thickness 0.6mm. The sections are interlocked with each other to form a equilateral triangle cell of size 300 mm x 300 mm x 300 mm.
11 | Metal Ceiling (Square Aluminium cell ceiling) | Providing and fixing Metal Open cell ceiling consisting of 0.5mm thick extruded aluminium metal of approved height in 'U' bends mounted using 6mm thk GI threaded rod suspended from true ceiling through anchor fasteners and hardware. The size of Openings will be 100 mm x 100 mm. Tile size 600X600 mm . Tiles to be fixed on 25X25 Al Grid . The System to be provided along the fleece backing with felt.Above ceiling services (ducts, tray, conduits) and true ceiling to be finished in black colour. Complete as per drawing and as directed by Engineer. Rate shall also include providing of acoustic fleece above the ceiling. Make: Armstrong / Hunter Douglas /Frameline/ Metal matrix is considered | sqm | 25 | 4682.5983 | 117064.9584 | Fameline make considered.
12 | True Ceiling Treatment & Paint finish | Providing and Applying Acrylic emulsion Paint of approved colour on the true ceiling surfaces of approved make, colour and shade in three coats , including preparing existing surfaces by scraping away and loose particles, dust etc., by washing and scrubbing, filling up with crack filler, binder; cleaning and making the surface dust-free, applying approved lambi-putty / POP punning and rubbing with sandpaper to make surface smooth to approval of the Project in-charge and applying a one primer coat and three coats of emulsion paint as recommended by approved paint manufacturer, including required scaffolding, cleaning and protecting till the handing over of site etc. all complete at all hei ghts and leads as per specifications or as directed by the Project in-charge to entire his satisfaction. All ceiling services to be painted and to be cleaned after completion of final coat painting . | Sqm | 80 | 318 | 25440
13 | Suspended Acostical pet panel board - Type-1 ( Café) | Providing and fixing of 50 mm thk eco panel boards in Honeydue shape of size 900x900 / 1200x1200mm approx. with necessary 18 mm thk ply backing for rigidity suspended from ceiling with suitable clutch wire support system that are height adjustable. Eco boards to be cut and installed to achieve the pattern as per detail dwg provided by Architect. Colour and other specifications are to be as per architects approval. Basic rate of Eco board - 1500/ sqm | Nos | 30 | 7748.0064 | 232440.192 | Quoted for 50mm thick eco board (BR: Rs.1,500/Sqm) with 18mm thick ply backing considered suspended from True ceiling.
14 | Suspended Cloud acoustical board ( Huddle space) | Providing and fixing acoustical cloud panels -( 800 X800 mm) . Basic price- Rs-7,500 . Make: Art & Design , Sensus, Rockworth | Nos | 10 | 5824.7424 | 58247.424 | Quoted based on the given basic price - Acoustic panel basic price Rs.7,500/Sqm.
15 | MS Work | Supply, Fabrication and installation of MS Structural Works of approved size, sections and shape as per the detailed drawing.The cost should include painting the members with one coat of primer and two coats of enamel spray paint of colour approved by Architect. Huddle area- Ceiling . Refer 3D view and submit cost proposal. | kg | 100 | 196.1 | 19610
G | FLOORING & DADO |  |  |  | 0
1 | LVT Flooring - | Supply and laying of 5-6 mm thk LVT Flooring over on self levelled PCC Floor. Basic rate LVT Floor - 300/ sqft . LVT to be cut and installed as per the pattern given in the detail dwg /3D view. | QRO-sqm |  | 4682.5983 | 0
2 | Anti-Static Raised Access Flooring With 600x600mm tiles (300 mm Height) ) - Server room, UPS & Battery room | Supply, fabricating and erection of 300mm height Antistatic Raised access flooring of size of 600mm x 600mm above finished floor level to withstand load of 1260 Kg per Smt. and rolling loads with Snap Lock Grid System using Electro-galvanized adjustable jack made out of 25mm dia. bright bar and 2 hr fire rated removable flooring tiles made of steel with non-combustible cementious compound complete in all respect as per the specifications. b. Provision should made for satisfactory earthing for all floor tiles.Cost Inclusive of One tile Puller. Make - Unitile | Sqm | 40 | 5141 | 205640
3 | 3M Recessed panel with Mat (Entrance, Cafeteria) | Providing and fixing floor Mat in nomad range of 3M make heavy duty Nomad range grey shade mat be fixed with Velcro. Basic price- Rs-6500/ sqm | Sqm | 10 | 7441.2 | 74412
4 | Granite Jambs | Providing and fixing of granite jambs formed of 19mm thick & 300mm to 350mm wide pre polished granite jambs and jambs to be fixed using necessary 1:4 cement mortar or adhesive as per details. Rate to include nosing as per architects instruction. Basic rate of Granite - 1800 per Sq.mt. | Rmt | 25 | 2884.896 | 72122.4
5 | Vitrified Tile Flooring -Type-1 -1200X2400 mm | Supply and laying of 1200 x 2400 mm Vitrified tiles laid over adequate thickness of cement mortar 1:4(1cement:4 coarse sand) without spacers , saint gobain weber epoxy grout , finished neat, allowing for necessary spacing for rubbing down the edges at corners..cost inclusive of removal of existing PCC screed floor and refill with PCC to match the tile floor level to Open office carpet floor . Includes protection with foam sheets with 2 layer of plastic cover after installation, deep cleaning before handover . Actual laid area shall be measured and paid for this item. Near door , Floor to be sunkened 12mm and finished with tile to install 3M Matt. Make- Kajaria / Asian - Basic price- 180 / sq ft . Make Epoxy Grout- Saint-Gobain Weber. | Sqm | 60 | 3253.1736 | 195190.4148
6 | Vinyl flooring | Providing & Laying of Vinyl Flooring over on cement plaster with smooth surface. Cost includes Self-Levelling Sub-Floor Cementitious floors of approved make, in thickness not less than 3mm, in approved colour shade with Surface preparation, Primer coat, Mixing, application, and properly designed joint treatment all as per manufacturer's specifications. Make: Armstrong Basic price- Rs-1500/ sqm. | sqm | 20 | 2409.804 | 48196.08
7 | Vitrified tiles flooring - Type-2 1200 x 600 mm / 600X600 mm - Café Passage , Handwash , Platewash | Supply and laying of 1200 x 600 mm / 600X 600 mm Vitrified tiles laid over adequate thickness of cement mortar 1:4(1cement:4 coarse sand) without spacers , saint gobain weber epoxy grout , finished neat, allowing for necessary spacing for rubbing down the edges at corners..cost inclusive of removal of existing PCC screed floor and refill with PCC to match the tile floor level to Open office carpet floor . Includes protection with foam sheets with 2 layer of plastic cover after installation, deep cleaning before handover . Actual laid area shall be measured and paid for this item. Make- Kajaria - Basic price- 90 / sq ft . Make Epoxy Grout- Saintgobain Weber. | Sqm | 60 | 2088.6853 | 125321.1186
8 | Vitrified tiles flooring - Type-3 300X 1200 mm - Cafeteria - Wooden Finish tile | Supply and laying of 1200 X 300 mm Vitrified tiles laid over adequate thickness of cement mortar 1:4(1cement:4 coarse sand) without spacers , saint gobain weber epoxy grout , finished neat, allowing for necessary spacing for rubbing down the edges at corners..cost inclusive of removal of existing PCC screed floor and refill with PCC to match the tile floor level to Open office carpet floor . Includes protection with foam sheets with 2 layer of plastic cover after installation, deep cleaning before handover . Actual laid area shall be measured and paid for this item. Make- Kajaria - Basic price- 100 / sq ft . Make Epoxy Grout- Saintgobain Weber. | Sqm | 50 | 2218.0729 | 110903.6448
9 | Rug | Providing and fixing 13mm thk customised rug as per selection. Basic price- Rs-6000/ sq m | Sqm | 10 | 7040.52 | 70405.2
0
H | SKIRTING & TRIMS |  |  |  | 0
1 | Aluminium skirting | Providing and fixing 75mm high Aluminium skirting of 1.5mm thick 75mm high extruded anodized aluminium skirting to be fixed with 12mm thk ply backing as per manufacture spec. as per Architects approval. (Make- Walline / Bottom Line/ Hysis ) | rmt | 450 | 307.4 | 138330 | Make - Bottomline considered
2 | Granite threshold-300mm | Providing and installing 19mm thick polished Granite ledge of 300mm wide, the exposed edge of the ledge shall be ground to full round shall polished to gloss. The ledge formed shall be installed over a 1:3 cement mortar bedding of average 25mm thick set in cement slurry, the joints shall be grouted in approved matching colour epoxy grout. Price quoted shall be inclusive of lead, lift, required stagging, scaffolding etc., complete as per detail drawing.. Basic rate of Granite - 1800 per Sq.mt. | rmt | 10 | 2843.6832 | 28436.832
3 | Granite threshold-100mm | Providing and installing 19mm thick polished Granite ledge of 100mm wide, the exposed edge of the ledge shall be ground to full round shall polished to gloss. The ledge formed shall be installed over a 1:3 cement mortar bedding of average 25mm thick set in cement slurry, the joints shall be grouted in approved matching colour epoxy grout. Price quoted shall be inclusive of lead, lift, required stagging, scaffolding etc., complete as per detail drawing.. Basic rate of Granite - 1800 per Sq.mt. | rmt | 20 | 4739.472 | 94789.44
4 | Aluminium corner guard | Providing and installing 18mm X 18mm corner guard installed using approved double side adhesive tape of 3M make, complete as per detailed drawing. Height - 2700 mm . Make: Wall Line/ Bottom line/ Hysys | Nos | 50 | 381.6 | 19080 | Make - Bottomline considered
5 | Window sill in prelam board finish | Providing and fixing 150-300 mm wide and 150 mm high factory made window sill made of 12mm thk ply and finished with approved 1mm thk Top . Cost inclusive of providing necessary wood / ply backing supports as per site condition. (Basic rate of the laminate is Rs 500/sqm). Make of Ply-Greenply, Archid ply, Century (MR-IS:303 -1989) . Make of Laminate - Merino, Greenlam, Century | rmt | 45 | 1325 | 59625
6 | Aluminium transition profile | Providing & fixing 8mm thk Aluminium Floor transition profile as per manufacturer specification. Sample to be submitted to Architect/Client for approval. Make : Wall Line / Bottom Line | rmt | 10 | 381.6 | 3816 | Make - Bottomline considered
I | FINISHES / PANELLING & BOXING |  |  |  | 0
1 | Laminate panelling | Providing and fixing Commercial ply panelling, of 12mm thk. ply panelling finished in 1 mm thick. of approved shade laminate with 6X6mm Aluminium U channel section to be inserted to achieve uniform groove between gypsum and panelling . (Basic rate of the laminate is Rs 550/sqm) Make of Ply-Greenply, Archidply, Greenply, Archid ply (MR-IS:303 -1989), Century Make of Laminate - Merino , Greenlam, Century ( Excluding Frame work - Ply to be fixed over Gypsum partition / External wall ) | Sqm | 150 | 2735.6232 | 410343.4858
2 | Lacquered glass panelling ( 12 mm thk ply + 6mm thk lac. Glass) | Providing and fixing Commercial ply panelling,12 mm thk ply panelling finished with 6mm thk approved shade Lacquered Glass with suitable adhesive as per manufacturers specifications . 6X6 mm aluminium profile section to be inserted b.w lac glass and other finishes as per detail dwg. Make of Ply-Greenply, Archidply, Century (MR-IS 303 -1989). Make of Glass - Saint Gobain Ultra White Lac. Glass | sqm | 50 | 4929 | 246450
3 | Eco panel board - 12 mm thk. | Supply and Installation of Modular acoustic panels /Tile (Eco Panel board) of size 1200mmx 2400mm. 12 mm thk Eco board to be fixed over on gypsum partition / Wall. Cost inclusive of providing 6X6 mm Aluminium "U" channel section to achieve uniform groove between gypsum and Eco board panelling. Eco boards to be cut and installed as per detail dwg provided by Architect. Basic Price - Rs.1650 / sqm. Make: Art & Design / Senses / Rock worth | Sqm | 25 | 3920.5636 | 98014.0912
4 | Eco panel board - 9 mm thk. | Supply and Installation of Modular acoustic panels /Tile (Eco Panel board) of size 1200mmx 2400mm. 9 mm thk Eco board to be fixed over on gypsum partition / Wall. Cost inclusive of providing 6X6 mm Aluminium "U" channel section to achieve uniform groove between gypsum and Eco board panelling. Eco boards to be cut and installed as per detail dwg provided by Architect. Basic Price - Rs.1250 / sqm. Make: Art & Design / Senses / Rock worth | Sqm | 25 | 3291.5962 | 82289.9054
5 | CNC Eco panel board - 12 mm thk. | Supply and Installation of CNC engraved Modular acoustic panels /Tile (Eco Panel board) of size 1200mmx 2400mm. 12 mm thk Eco board to be fixed over on gypsum partition / Wall. Cost inclusive of providing 6X6 mm Aluminium "U" channel section to achieve uniform groove between gypsum and Eco board panelling. Eco boards to be cut in CNC and installed to achieve the pattern as per detail dwg provided by Architect. Basic Price - Rs.2300 / sqm. Make: Art & Design / Senses / Rock worth | Sqm | 85 | 5034.7345 | 427952.4345
6 | Printed Eco board -12 mm thk | Supply and Installation of 9 mm thk Printed Eco Panel board of size 1200mmx 2400mm. 12 mm thk Eco board to be fixed over on gypsum partition / Wall as per manufacturers specification. Cost inclusive of providing 6X6 mm Aluminium "U" channel section to achieve uniform groove between gypsum and Eco board panelling. Eco boards to be cut and installed to achieve the pattern as per detail dwg provided by Architect. Make: Art & Design Make: Art & Design / Senses / Rock worth. Basic Price - Rs.1800 / sqm | Sqm | 15 | 4109.2539 | 61638.8081
7 | Ply boxing finished with Laminate | Providing and fixing 200-300 mm thk ply boxing made of 12mm thk Commercial ply fixed on suitable Aluminium / Ply wood frame work in intervals of 600mm horizontally and vertically, finished with 1mm thick approved shade Laminate with grooves as directed. (Basic price of Laminate is Rs 1000/sqm). Make of Ply-Greenply, Archidply, Greenply, Archid ply ( MR-IS:303 -1989), Century Make of Laminate - Merino, Greenlam, Century | Sqm | 25 | 3783.0466 | 94576.1638
8 | Pelmets | Providing and fixing pelmets made of 18mm Pre laminated ply of size 200X300 / 300 x 300mm wide along windows and glazed area and with necessary Aluminium frame work/ wood support, and also to mount the Blinds and Pull Down screens. The edges on the glazing side has to finished with enamel paint / Edge banding . Vertical support Ply to be anchored to the structural beam. Fixing detail may vary as per site conditions. Make of Ply- Archid ply, Green ply, Century | Rmt | 60 | 1272 | 76320
9 | Ply backing for mineral fibre tiles | Providing and fixing 6mm thick commercial ply backing of 600mm x 600mm on mineral fibre modular false ceiling tiles to support light fitting, speakers, CCTV cameras, diffuser of grid work size with necessary cut outs for the same. Make of Ply-Greenply, Century, Archidply, Century (MR - IS : 303 - 1989). | Nos | 100 | 951.923 | 95192.2951
10 | Plywood panelling (Without frame work) |  |  |  | 0
| 6 mm thk | Providing and fixing 6 mm thk comm. Ply panel over on Plywood/ Gypsum partition / Existing Wall | Sqm | 10 | 951.923 | 9519.2295
| 12mm thk | Providing and fixing 12 mm thk comm. Ply panel over on Plywood/ Gypsum partition / Existing Wall | Sqm | 50 | 1469.4733 | 73473.6647
| 18 mm thk | Providing and fixing 18 mm thk comm. Ply panel over on Plywood/ Gypsum partition / Existing Wall | Sqm | 10 | 1792.9423 | 17929.4226
11 | Logo ( Reception) | Providing and fixing " Photon " Logo with back lit LED - made of 12 mm thk Imported Acrylic with laser cut and duly painted with ducco as per brand colour. Logo Height- 450 mm . Warranty - 3 Years . | Nos | 1 | 47700 | 47700
12 | Gypsum Boxing finished in paint | Providing and fixing Gypsum Boxing of 12mm thk. Gypsum fixed to frame work & level, Niches to be finished in plastic emulsion paint as per selection 8mm Aluminium channel section to achieve uniform groove between gypsum and wall. (Basic price of Gypsum is Rs 160/sqm) - Make of Gypsum - India Gypsum, La Gyp. | Sqm | 10 | 1442.6716 | 14426.7158
13 | Steps | Providing and fixing Step for Hub room,UPS roomin 18mm thick fire rated ply finished with anti-skid laminate with necessary hardwood honeycomb framework with necessary related works. Includes 18X18 mm Aluminium Edge profile in edges . | Sqm | 5 | 4081 | 20405
14 | Concealed corian marker holder | Providing and fixing concealed marker holder of size 150mm Ht x 75mm D x600mm Length , made of 12 mm thk corian to be cladded over on Aluminium frame work with necessary ply backing as per detail dwg/ Ref Image. Basic Rate of corian Rs. 500/ sq ft. Make of Corian - Staron, Merino, LG | Nos | 12 | 1272 | 15264
15 | Suspended MS frame work with weld mesh finish | 40X20mm MS frame work with interconnector frames and weld mesh covering to hold suspended artificial plants . Refer detail dwg and submit cost proposal for this item | QRO-Sqm |  | 6890 | 0
16 | MS support works | MS angle support works for special ceiling , MS frame planter frames ,etc.,Supply and Fabrication of MS angles , Box sections and MS plates . | Kg | 100 | 196.1 | 19610
17 | MDF Grooved Fluted panel | Providing and fixing 18mm thk Grooved MDF Fluted panel in Ducco paint finish. MDF to be fixed over on 600X600 mm Aluminium grid frame work and 12mm thk base ply . | sqm | 25 | 4805.8246 | 120145.6152
18 | Veneer Panelling | Providing and fixing Commercial ply panelling, of 12mm thk. ply panelling finished in 4 mm thick. of approved shade veneer with 6X6mm Aluminium U channel section to be inserted to achieve uniform groove between two finishes (Basic rate of the laminate is Rs 1500/sqm) Make of Ply-Greenply, Archid ply, Century (MR-IS:303 -1989) . Make Veneer- Century, Greenlam | QRO-sqm |  | 3900.1115 | 0
19 | Fabric Panelling | Providing and fixing Fabric Panelling with Jolly Board to be wrapped with approved Fabric to be fixed over on 12 mm thk commercial ply panelling . The rate should includes 3mm thk recron foam and approved gripper system. Cost inclusive of providing 6X6 mm Aluminium "U" channel section to achieve uniform groove between gypsum and Fabric panelling. (Basic rate of fabric - Rs.750 / rmt) Make of Fabric - D Decor | QRO-sqm |  | 7950 | 0
20 | Green Moss wall | Providing and fixing Natural Green Moss wall as per Architects selection. Basic price - Rs-2500 /sqft | Sqm | 10 | 30806.568 | 308065.68
21 | Artificial Green wall | Providing and fixing Artificial Green wall as per Architects selection. Basic price - Rs-500 /sqft | Sqm | 10 | 6161.3136 | 61613.136
22 | Fire Clay Brick cladding | Providing and fixing Fire clay Brick Cladded with Cerabond adhesive on to the levelled surface of the wall / Column / Gyp partition. Cost inclusive of levelling of wall surface and providing 12 mm thk Bison board backing on existing double skin Gyp partition / Wall / Aluminium frame work. Grooves to be spaced with the spacers and finished with cement grout material of approved colour. | Sqm | 30 | 4386.8553 | 131605.6585 | Fire clay brick Basic price Rs.160/Sqft. Considered as per the query response.
23 | Mdf Groove wood acostic perforated panel | Providing and fixing PAX- GROOWOOD Perforated panels of width 128mm, thickness of 15mm and length of 2440mm or as per detail dwg , made of a High density moisture resistant fibre board substrate with laminated/Melamine facing as per the approved shade / species and finish and a melamine balancing layer over the reverse side. The board shall have a special perforated pattern where the visible surface has a “Helmholtz” fluted perforation of 2mm width and 15mm or 30mm each. The Back side of each panel is being perforated with 8mm round hole for superior acoustic performance. Installation : Installed on specially extruded aluminum sections of 25 mm duly fixed using screws and plugs spacing at 600mm c/c. Place the GROOWOOD clip to install the first set of wooden panels by inserting the clips for border and insert the groove of panel into projecting flange of aluminium clip. Continue installing rows of panels by inserting the tongue into the groove of earlier inserted panel and progressively installing clips for inside into the next keel till the actual height is achieved. Use clips for the border to finish off the installation. Edges should be finished using wooden moulding of matching colour.as per manufacturers specification . Make: Gyptech , Art& Design - Groove wood panels | Sqm | 10 | 7393.5763 | 73935.7632 | Quoted for the Basic price - Rs.600/sft. as per the query response.
24 | Bison board panelling | Providing and fixing 12 mm thk bison board over on 600X600 mm Aluminium frame work. ( Cost to be quoted excluding frame work) | Sqm | 10 | 1330.8437 | 13308.4374
25 | Pine wood planks cladding | 12mm thk pine wood planks to be cladded on café column with suitable ply backing support. Pine wood surface to be treated and finished with PU matt polish . Edges to be covered with 25X25 MS L angle frame in black enamel finish . Refer 3D view and submit cost proposal | QRO-Sqm |  | 10070 | 0
26 | Architrave in corian finish | 50 mm thk and 300 mm deep architrave made of 12mm thk ply around main entrance door and finished with approved 12mm thk corian . Basic rare corian - 750 / sqft | Rmt | 10 | 7670.8354 | 76708.3543
I-1 | COLUMN FINISHES |  |  |  | 0
1 | Column Cladding | Providing and fixing 25X25 Aluminium Box sections all around column with suitable ply backing . Al sections to be fixed in 600X 600 mm grid form to make align the column 90 Deg all 4 corners . 18X18 mm Al. corner guard to be fixed to all columns after following finishes . ( Height - 2800 mm) |  |  | 0
A | laminate finish | With ref spec 20 - 12mm thk ply to be cladded to the Aluminium frame work and finished with 1mm thk approved laminate . Make of Ply-Greenply, Archidply, Greenply, Archid ply ( MR-IS:303 -1989), Century Make of Laminate - Merino, Greenlam, Century | Sqm | 25 | 3718.3528 | 92958.8189
B | Lac. Glass Finish | With ref spec 20 - 12mm thk ply to be cladded to the Aluminium frame work and finished withapproved 6mm thk lac. Glass . Make of Ply-Greenply, Archidply, Century (MR-IS 303 -1989). Make of Glass - Saint Gobain Ultra White Lac. Glass | Sqm | 15 | 6432.4114 | 96486.171
C | Eco board | With ref spec 23 - 12mm thk ply + 9 mm thk CNC cut engraved Eco board to be cladded to the ply panel . Basic price-2500/sqm . | Sqm | 20 | 6614.1701 | 132283.403
D | Vinyl Poster | With ref spec20 - 12mm thk ply + 12.5 mm thk plain gypsum board to be cladded to the Aluminium frame work and finished with approved 3M vinyl poster with 5 years warranty . Make-3M | Sqm | 30 | 5820.2849 | 174608.5468 | Vinyl poster basic price Rs.190/Sft. considered as per the query response.
0
J | STORAGES & SHUTTERS |  |  |  | 0
1 | Trap door - Above ceiling services | Providing and fixing trap door of size 600 x 600mm - Make - Knauf. | Nos | 15 | 4770 | 71550
2 | Trap door in PVC - Ac units - 1800X900 mm | Providing and fixing PVC trap door for A/c units in PVC of Elgi or equivalent make with all hardware's, locks etc. complete. Cost includes providing necessaey Ply wood frame work support from true ceiling . Size -1800X900 mm | Nos | 2 | 7950 | 15900
3 | Junction box cover | Providing and fixing junction box cover in Various size from 150x150mm to 600mmx600mm of 19mm thick. commercial ply with necessary seasoned wood framework to prepare levelled surface for carpet. Including of civil work neatly finished and levelled around the junction box. Cost includes deep cleaning the junction box before start of carpet installation as per PM directions . | Nos | 75 | 689 | 51675
4 | Low Height. Storage in Laminate Finish (600 Deep) | Providing and fixing factory made Low height storage made of 19mm ply finished with 1mm thk laminate of approved shade . Storage Sides, front, bottom, intermediates, & shutters to be formed of 19mm ply finished with approved 1mm thk laminate . Shutter to be fixed with all necessary accessories like SS soft close hinges, tower bolts, locks (multi-purpose), Brushed SS handle, ball catches all complete., as directed by Architect / PM. Provide 5 Nos adjustable shelf made of 19mm ply finished with 1mm laminate. To have 12mm ply backing finished with laminate of approved colour as per details. Make of Ply - Century, Green Ply, Archid Ply; Make of Laminate- Merino, Greenlam. Basic price Laminate - 550/ sqm . make Fittings - Hettich / Hafele | Sqm | 25 | 15403.284 | 385082.1
5 | Low Height. Storage in Laminate Finish 450 Deep - Height - 900 +150 mm planter box . | Providing and fixing factory made Low height storage made of 19mm ply finished with 1mm thk laminate of approved shade . Storage Sides, front, bottom, intermediates, & shutters to be formed of 19mm ply finished with approved 1mm thk laminate . Shutter to be fixed with all necessary accessories like SS soft close hinges, tower bolts, locks (multi-purpose), Brushed SS handle, ball catches all complete., as directed by Architect / PM. Provide 5 Nos adjustable shelf made of 19mm ply finished with 1mm laminate. To have 12mm ply backing finished with laminate of approved colour as per details. Make of Ply - Century, Green Ply, Archid Ply; Make of Laminate- Merino, Greenlam. Basic price Laminate - 550/ sqm . make Fittings - Hettich / Hafele . Storage Height- 900+150 mm . | Sqm | 15 | 12938.7586 | 194081.3784
6 | DB shutters | Providing and fixing 25mm thick laminated shutter Size - 600 - 750mm finished with approved laminate shade, inside face of shutter to be finished in 1mm thick laminate of approved shade inclusive of providing & fixing of 300X200 mm Aluminium Grill finished in approved shade powder coating for ventilation, approved 200mm high SS concealed handle etc complete as directed. Cost includes providing necessary frame work in Ply wood and Alu. Frame support as per site condition . Make of Ply-Greenply, Archidply, Greenply, Archid ply ( MR-IS:303 -1989), Century Make of Laminate - Merino, Greenlam, Century | Sqm | 20 | 9241.9704 | 184839.408
0
K | LOOSE FURNITURES |  |  |  | 0
1 | Reception Table | Providing and fixing of Security table of size 2400 (L) x 900 (D) X 1050 (H)mm, as per detail drawing. Table made up of 18mm thk ply finished with laminate and solid acrylic surface. Table front fascia 2400mm X 1050 mm, side 900 mm X 1050 mm and Top surface 200 x 2400 mm to be finished with approved Solid acrylic surface with thermoforming and veneer as per detail dwg. Table inner surface to be finished with frosty white unicolor laminate, inclusive of 1 No 3 drawer mobile Pedestal (1P+2F), 25 mm thk laminated top, Wire manager, Slow Close hinges and drawers (Basic rate of the laminate is Rs 550/sqm) Make of Ply-Greenply, Sharon, Archidply. Make of Laminate - Merino, Greenlam, Century. Make of Corian - Staron / LG/ Merino . Basic price - 900 / sq ft ; Make of Uni color Laminate- Merino. Basic price - 1000/Sqm . | Nos | 1 | 174900 | 174900
2 | Slotted Angle rack | Providing and fixing heavy duty slotted angle full height storages of 450mm wide and 2100 high with four equal portion with covering partition on the top, with construction of 6 bend on its profile with thickness of 1.6 - 1.8mm. it should be rolled form single piece without any bend.Vertical member - it should have flexibily for adjustment. Horizontal menber - It should be roll form with 2 profile with height of 85mm and 1.6 mm thickness , The beam should not exceed deflection of tan/200. Panel should be roll form with 6 bends. the material should be .8 thk or 1mm thk design to carry uniformly distributed load with MS Powder coated as per the colour selected by the architect/ client. | Rmt | 10 | 7950 | 79500
3 | IT Store rack | Providing and fixing heavy duty full height storages made of ply and finished with the approved laminate of 600mm wide and 2100 high with four equal portions with covering partition on the top. | Rmt | 5 | 15403.284 | 77016.42
4 | 450+450 mm high raised platform ( 450 & 900 mm = 2Levels ) | Raised platform to be made by using 50X50 MS square box sections in 600X600 mm Grid frame finished with 25mm thk ply to form a 2 level step seating . Ply surface to be finished with approved 12mm thk rubber wood panels and finished with PU matt polish . Cost includes providing seat cushion and throw pillows - 6 Nos . cost includes providing cove light provision in vertical boxing - 75+75mm . basic price throw pillows - Rs-2,000 . make- D'Decor | Sqm | 5 | 12190 | 60950
0
L | PARTITION / WALL FINISHES |  |  |  | 0
1 | Asian Royal Matt emulsion | Providing & applying Asian Royal Matt Paint of approved shade and colour of Asian Paints in minimum three coat, including preparation of surface, scrapping, sand papering, scaffolding, Putty, Primer etc complete. Make : Asian / Dulex | Sqm | 900 | 296.8 | 267120
2 | Concrete texture paint finish - Cabin | Providing and fixing cement texture paint with buttons as per the following specification. * Providing and applying / installing one coat of primer (as per manufacture recommendations) * Providing and applying / installing of micro concrete in a desired shade. * Sanding with 120 & 180 grit. * Providing and applying / installing multiple coats of GFS sealer system for stain protection. Basic Price of cement texture finish is Rs - 150/sft | Sqm | 25 | 1848.3941 | 46209.852
M | FILM / POSTERS/ ART WALLS |  |  |  | 0
1 | Printed UV Frost Film | Printed UV Film - Supply and fixing of dots pattern printed with UV white ink on ultra clear film - basic price Rs. 1800 / smt | Sqm | 50 | 2232.36 | 111618
2 | Frost Film | Providing and fixing 3M make frost film- 7725 | Sqm | 5 | 2365.9444 | 11829.7221 | Basic price Rs.180/Sft considered as per the query response.
3 | Wall paper | Providing and fixing Commercial grade Wall Paper of approved shade with recommended Adhesive of approved make which have 100% washable, Scratch resistance, Peel proof, & fire retardant properties. Cost to include preparation with Primer and 1 coat of emulsion on the punned surface/partition for receiving the wall paper as per the manufacturer specification. (Basic Price - 1000 / Sq.mt ) | Sqm | 25 | 1522.584 | 38064.6
4 | Vinyl poster | Providing and fixing 3M Vinyl graphics on wall with 5 yrs warranty as per the manufacturer specification. Cost to include preparation with Primer and 1 coat of emulsion on the punned surface/partition for receiving the vinyl poster as per the manufacturer specification. Cost including design charges as per Architect / Client instructions . Make:3M | Sqm | 220 | 2735.6232 | 601837.1124 | Basic price Rs.190/Sft considered as per the query response.
5 | Artwork | Handmade mural /painting on high quality oil canvas and pigment as back drop as per the approved Theme and size , to be done by a professional artist. Artworks to be done directly on masontry wall / Gypsum partition , the base wall surface to be finish properly as free from oil, dust, stayings etc.. Cost to include installation and any incidentals required to complete the work.. Sample to be approved by the Architect/ client. . Basic rate- 500/sq ft. | Sqm | 25 | 6161.3136 | 154032.84
6 | Sun control Film - | Providing & fixing 3M Suncontrol 3M Scotchtint NV-15 Night Vision Series Films Solar Heat Reduction: 69%, Glare Reduction: 83%, UV Blocked: 99%, Visible light transmitted: 15%, Total Solar Energy Rejected: 77%, Color: Brownish. | Sqm | 60 | 3228.5283 | 193711.6996 | Basic price Rs.250/Sft considered as per the query response.
7 | 3M White board Sticker | Supply and fixing of 3m WH11 Writing vinyl with bubble free application on the wall prepared with smooth finish and oil based primer. Make:3M | Sqm | 175 | 4128.0801 | 722414.0196 | Basic price Rs.320/Sft considered as per the query response.
0
N | BLINDS |  |  |  | 0
1 | Block out roller blinds | Providing and fixing Block out roller blinds with drive unit end plug support brackets roller tube bottom rail ball chains all described as below but with fabric of approved shade color and sample. Drive unit to be of moulded plastic with straight rectangle support pin and inserted into the tube end. It shall be driven by a ball chain pully and can be positioned at right or left side of the shade. The shade when lowering or raising shall automatically be lockable from release of the ball chain by means of friction lock. End plug shall be moulded to plastic locking pin. The plug shall be inserted into the tube end. Support brackets shall be of zinc plated steel and provided with moulded plastic covers and used in right of left hand positions differentiated by acceptance of the rectangular drive unit support or the ground idler plug pin. Roller tube shall be made out of roll formed steel of thickness suitably protected against corrosion and keyway integrated with the tube to accommodate the spline, outside diameter of the roller tube shall be 25mm. Bottom rail shall be stiffening element inserted into the bottom rod pocket. Tube to be of the material as approved out of timber, PVC, Steel of VB Bottom rail. Ball chain shall be of 2mm dia cord with actual balls moulded coaxially to it on 6mm pitch to form ball chain. Gap above pelmet to be covered and finished with Approved Gypsum cladding .Make - Vista EP 001 /Eq in Hunter Douglas . | Sqm | 110 | 843.1818 | 92750 | Vista make considered. | 105.3 | 88787.0455
0
0 | SIGNAGES |  |  |  | 0
1 | Room indicator | Supply and fixing of room signage made of 2m thick acrylic laser cut with fine edges and installed on the door with 3m double sided tape basic price- Rs. 4000/no | Nos | 25 | 4579.2 | 114480
2 | Pull push signage (1 set) | Supply and fixing of push / pull signage of size 4"x1" formed of SS plate with engraved letter fixed onto the door with suitable adhesive. | Nos | 25 | 689 | 17225
3 | No entry to unauthorised persons | Providing and fixing 3mm Room signage in Acrylic with ducco paint, the names will be on 2mm acrylic laser cut, signages will be fixed on 3m double sided tape. | Nos | 4 | 954 | 3816
0
P | CAFETARIA FINISHES |  |  |  | 0
1 | Water proofing | Providing, supplying, mixing and applying two coats of ready-to-use two-component acrylic polymer, modified cement base, flexible water-proofing slurry or approved equivalent to a thickness of 2 mm over the bottom and sides of the slab / sunken slab. Water proofing to extend upto 600 on the preiphery walls. Cost to include checking of water proofing for 48 hours with 300mm high water logged floor. Method Statement of water proofing to be submitted before execution. Only floor area shall be measured and paid for this item. | sqm | 50 | 954 | 47700
2 | Wash basins - Counter Sunk | Providing and fixing rectangular below counter wash basins, waste coupling. Cost incl. of providing and fixing of bottle traps, Teflon tape etc.. Make Wash basin - Parryware - Rectangular wash basin . PARRYWARE Havana N Series Under Counter WASH Basin | Nos | 2 | 10474.92 | 20949.84
3 | Sink with Sink cock | Providing and fixing 550X450 mm SS Sink with Long body pillar cock. Make Parryware new coral -WPC854899 . Sink cock- Parryware PRUNO Swan Neck Pillar Cock for basins ¦ Single-Lever Deck Mounted with Honeycomb Type Aerator ¦ T5803A1 | Nos | 1 | 17490 | 17490
4 | Piller cock for wash basins | Providing and fixing in position Toilet Piller cock . Make: Parryware - Sensor Tap -Parryware G541PA1 E-Taps Deck Mounted Pillar Cock | Nos | 2 | 12190 | 24380
5 | Wash basin counter- Corian finish | 600 mm wide, 800 mm high wash basin counter made of 18mm thk WPC / PVC integral board , MS angle support finished with 12mm thk corian . Cost includes 100 mm high band above counter and 300 mm high front fascia as per detail dwg. Necessary cutout to be made in counter top to fix the counter sunk washbasins and sink . Basic price corian - 900/sqft . | Sqm | 3 | 19610 | 58830
6 | Corian top storage counter ( Café) - Vending machine counter,Juice counter. | Providing and fixing storage unit with 600mm wide 50 mm thk Corian counter top of approved shade corian to be fixed over on storage made of 18mm thk WPC / PVC integral board. Storage inner surface to be finished with white laminate and shutters to be in laminate finish with finger groove profile handle as per detailed drawing. Cost inclusive of 200mm high Corian band above storage unit to mount powet / data sockets as per detail dwg . Make of Ply - Greenply, Archidply . Make of Laminate - Merino, Greenlam, Century . Make of Corian - Staron, LG, Dupont . Basic rate of corian - 900 / sqft | Sqm | 5 | 23850 | 119250
7 | Over head Storage in Laminate Finish (450 Deep) - Cafeteria | Providing and fixing Above Storage of 600 mm high and 450mm deep with 18mm thk finger groove laminated shutters - made of 18mm thk Ply and finished in 1mm thk Laminate (Inner & External Surface to be finished in approved 1mm thk Laminate). Storage top to be finished with 50mm thk corian top. Rate to include Hafele /Hettich make locks, one number Adjustable Intermediate shelf, Soft Close hinges - 2 Nos for shutters, Finger Groove on handle , magnetic ball-catch, Tower Bolt etc complete as directed. Make of Ply - Century, Green Ply, Archid Ply; Make of Laminate- Merino, Greenlam. Basic price Laminate - 550/ sqm FSC CERTIFICATION TO BE PROVIDED | Sqm | 5 | 17490 | 87450
8 | Low ht partition for Coffee Shop Counter - 1050mm Hight - 300 wide corian top - Bison board box with Solid wood+ Tile finish | Providing and fixing 100 mm thk, 1050 mm high boxing made of 10 mm thk Bison board . Bison board to be cladded over on 50X25 mm MS box section grid frame grouted to the floor. Internal and External surface of the boxing to be cladded with approved wall tiles of basic price-150/ sq ft . with 3mm spaces and Tile adhesive . Cost includes providing 300 mm wide and 50 mm thk Corian top as per detail the detail dwg provided by the Architect. Basic price of Corian : 750/ sqft . Basic price Tile - 150 / sqft ; Make- Asian / kajaria . Make adhesive and grout - Weber ( Saint gobain) | sqm | 2 | 16635.5467 | 33271.0934
9 | Low ht partition for Bainmarie - 850mm Hight - 150 wide corian top - Bison board box + Tile finish on either sides | Providing and fixing 100 mm thk, 850 mm high boxing made of 10 mm thk Bison board . Bison board to be cladded over on 50X25 mm MS box section grid frame grouted to the floor. Internal and External surface of the boxing to be cladded with approved wall tiles of basic price-150/ sq ft . with 3mm spaces and Tile adhesive . Cost includes providing 300 mm wide and 50 mm thk Corian top as per detail the detail dwg provided by the Architect. Basic price of Corian : 750/ sqft . Basic price Tile - 150 / sqft ; Make- Asian / kajaria . Make adhesive and grout - Weber ( Saint gobain) | sqm | 2 | 14171.0213 | 28342.0426
10 | Wall tile- 600X600 mm / 600X300 mm - Platewash , Handwash | Providing and fixing wall tile 600X600 / 300X600 mm . Fixed with 3mm spacers, adhesive and epoxy grout . Basic price tile - 80/ sqft . | Sqm | 80 | 2144.1371 | 171530.9706
11 | Wall tile- 300X100 mm / 300X300 mm / 600X300 - Servering counter , Juice counter rear wall | Providing and fixing decorative wall tile 300X100 /300X300 / 300X600 mm . Fixed with 3mm spacers, adhesive and epoxy grout . Basic price tile - 120/ sqft . | Sqm | 30 | 2661.6875 | 79850.6243
12 | Architrave Jamb in Granite finish (Café wash area entrance ) | Providing & fixing Granite architrave of size 200mm wide 19mm thk on café Hand wash Basic Price 19mm thk Granite - INR 1800 / Sqmt. | Rmt | 15 | 1854.576 | 27818.64
13 | Running counter - Café- Corian finish | Providing and fixing running counter in corian finish , wide 600 mm, thickness 50 mm.corian panel to be be fixed to the wall and floor with suitable MS bracket . Cost includes providing 200 mm high , 25 mm thk corian band above the running counter . MS brackets to be finished with approved ducco paint . Basic price of Corian - 800/ sqft . Make of Marine ply- Century, Green, Archid | Rmt | 5 | 15582 | 77910
14 | Core cutting | 150 mm dia core cut . Includes Slab structural scanning and cover the gaps with fire sealent after completing the works | Nos | 2 | 1961 | 3922
15 | Suspedned MS frame work with weld mesh finish | 50X25mm MS frame work with interconnector frames to hold suspended artificial plants . Refer detail dwg and submit cost proposal for this item | Sqm | 15 | 5914.8611 | 88722.9158
16 | SS 304 Food Bainmerry - 4 holes With Acrylic Sneeze Guard (Without Railing) | 1/1-150mm depth GN Pan with lid- 4 nos, Size: 1850X 750 MM Unit Top Made Out Of 16 Swg Ss Sheet 1 Under Shelf And Three Sides Covering Made Out Of 18 Swg SS Sheet. Unit Legs Made Out Of 16 Swg 1.5" Sq Pipe. Bain Marie Tank Made Out Of 16 Swg Ss Sheet With Proper Argan-Arch Welding With 0.75" Drain Outlet Valve With Fittings. 1 set Electrical Load 3Kw Make Water Heater With On/Off Switch, 0 To 110 Degree Thermostat Control With Indicator Lamps | Nos | 1 | 132500 | 132500
17 | SS Chute Table | SS 304 Grade Materials 1300 X 450 MM | Nos | 1 | 23320 | 23320
18 | SS Plate rack | SS 304 Grade plate rack - 300mm (D) X 900 mm(W) X 2100 mm ( Ht). With Adj.shelves | Nos | 1 | 29680 | 29680
19 | SS Loading Table | Sink Size: 850 X 600 MM SS 304 Grade Materials | Nos | 1 | 40280 | 40280
20 | 2 SS Holes Spoon sterilizer 50+50 Spoon | storage-Material Of Construction : Made Out Of 304 Quality 16g Thickness Stainless Steel Sheet. Holder : 2nos sqaure Perforated Spoon Holder Will Be Provided. Control Panel : Toggle On /0ff Switch With Pilot Lamp Indicator. | Nos | 1 | 27560 | 27560
0
Q | MISCELLANEOUS |  |  |  | 0
1 | FRP Planter box | Supply and placing of FRP planter box |  |  | 0
|  | Type-1 . Basic Price - Rs-2,500 | Nos | 2 | 2862 | 5724
|  | Type-2 . Basic Price - Rs-3,500 | Nos | 6 | 4006.8 | 24040.8
|  | Type-3 . Basic Price - Rs-4,500 | Nos | 8 | 5151.6 | 41212.8
0
2 | Plants - Artificial | Supply and installation of Imported Artificial plants as per design and selection . |  |  | 0
|  | Type-1 . Basic Price - Rs-5,000 | Nos | 2 | 5724 | 11448
|  | Type-2 . Basic Price - Rs-7,000 | Nos | 3 | 8013.6 | 24040.8
|  | Type-3 . Basic Price - Rs-12,000 | Nos | 4 | 13737.6 | 54950.4
|  | Type-4- Basic Price - Rs- 500 | Nos | 100 | 572.4 | 57240
3 | Plants - Natural | Supply and installation of Natural plants as per design and selection . |  |  | 0
|  | Type-1 . Basic Price - Rs-6,000 | Nos | 2 | 6868.8 | 13737.6
|  | Type-2 . Basic Price - Rs-7,000 | Nos | 2 | 8013.6 | 16027.2
|  | Type-3 . Basic Price - Rs-8,000 | Nos | 4 | 9158.4 | 36633.6
|  | Type-3 . Basic Price - Rs-550 | Nos | 75 | 629.64 | 47223
0
4 | Throw pillows | Supply of throw pillows of size 600X600 mm size . Fabric Make - D'Décor . Basic Price - 600 / sqm | Nos | 8 | 1590 | 12720
R | HOUSE KEEPING & DEBRIS REMOVAL |  |  |  | 0
1 | House Keeping & Debris removal | House Keeping / Debris removal - Keeping the site reasonably clean and removal of debris from the site every day. Should also provide for thorough cleaning of site before handover .Should also include final cleaning of site before handover to client. Cost inclusive of Cleaning the Existing Glazing Internally, Thresholds, Existing Doors Internally and cleaning , Existing AHU , Lobby, Electrical room cleaning . All existing finished surfaces in the floor. Housekeeping : Dedicated collection and storage area with individual bins to be provided for collection of different type of waste as per Construction and Demolition Waste Management Plan. Collected waste to be disposed out of the site on regular basis (daily or alternative days). Vendor should ensure that debris, dust, dirt created by each and every vendor to be cleared by Housekeeping workers. There should be at least one vacuum cleaner of industrial type to be given for Housekeeping workers. Shifting of debris from site to designated area outside of site by trucks or tempo is also in the scope of House keeping works. Providing housekeeping agency for general housekeeping works . Please note that this house keeping people would be responsible for only general housekeeping and monitored and controlled by Project Managers at site. Should also provide for thorough cleaning of site before laying of carpets. Should also include final deep cleaning of site before handover to client. Man power not less 7 Person along with a supervisor for 18 Hours per day (two shifts), one dedicated qualified site engineer to be allocated for monitoring the safety measures. Debris removal : Removal of debris in truck from the specific location in the site and disposing the same from building premises on daily basis as per the instruction given by the PM / Base builder. Lumsum cost to be quoted for this item. | LS | 1 | 212559 | 212559
Total | [5 empty] | 20485551
Grand Total ( EXCLUSIVE OF TAX) | [5 empty] | 20485551

## REST ROOM
RESTROOM BOQ
S.NO | Item | Specification | Make | Unit | Total Qty | Rate | Amount | JLL Remarks
1 | 150mm thick Aerocon wall | Making 150mm thick wall of Aerocon Block in 1:4 cement mortar, inclusive of 12 mm thick single coat rough Cement Plaster on both sides of wall in 1:6 Cement Mortar,with 2 nos. of 8 mm diameter steel reinforcement in every 4 layer & 2 nos. of hoop iron strips 25mm x 1.6mm, painted with anti-corrosive paint, RCC Lintel at 2400 mm Ht, properly bent and bonded at the end, inclusive of shuttering, scaffolding, Raking of joints and proper curing etc complete. The joints between the RCC and masonry will have hold fasts @ 600mm c/c, with joints finished in chicken mesh 20 gauge and finished with cement plaster |  | Sqm | 85 | 2597 | 220745
2 | 100mm thick Aerocon wall | Making 100mm thick wall of Aerocon Block in 1:4 cement mortar, inclusive of 12 mm thick single coat rough Cement Plaster on both sides of wall in 1:6 Cement Mortar,with 2 nos. of 8 mm diameter steel reinforcement in every 4 layer & 2 nos. of hoop iron strips 25mm x 1.6mm, painted with anti-corrosive paint, RCC Lintel at 2400 mm Ht, properly bent and bonded at the end, inclusive of shuttering, scaffolding, Raking of joints and proper curing etc complete. The joints between the RCC and masonry will have hold fasts @ 600mm c/c, with joints finished in chicken mesh 20 gauge and finished with cement plaster |  | Sqm | 10 | 2491 | 24910
3 | Aerocon light weight blocks filling | Aerocon Light weight blocks filling up to 200-300 mm depth. cost inclusive of Providing top layer in 50 mm thk Grano Flooring.to receive tile floor |  | Sqm | 50 | 3074 | 153700
4 | Cinder filling | Providing and laying of raised floor 300mm deep with necessary cinder with 25-50mm thk 1:2:4 grade PCC concrete, curing 2 days and then finishing the surface with 10mm thk of 1:6 mortar to proper level and slope. Rate to include necessary steps and ramp as per architects instructions. |  | Sqm | 20 | 2597 | 51940
5 | Water proofing | Providing, supplying, mixing and applying two coats of ready-to-use two-component acrylic polymer, modified cement base, flexible water-proofing slurry or approved equivalent to a thickness of 2 mm over the bottom and sides of the slab / sunken slab. Waterproofing to extend upto 600 on the preiphery walls. Cost to include checking of waterproofing for 48 hours with 300mm high water logged floor.Method Statement of water proofing to be submitted before execution. |  | Sqm | 100 | 954 | 95400
6 | 150mm thick Ledge wall | Making 150mm thick ledge wall of Aerocon Block in 1:4 cement mortar, inclusive of 12 mm thick single coat rough Cement Plaster in 1:6 Cement Mortar |  | Rmt | 20 | 2650 | 53000
7 | Vitrified tiles flooring 1200x600 MM for toilet | Supply and laying of 1200X600 mm Vitrified tiles laid over adequate thickness of cement mortar 1:4(1cement:4 coarse sand) with 3mm thk spacers , saint gobain weber epoxy grout , finished neat, allowing for necessary spacing for rubbing down the edges at corners.. Includes protection with foam sheets with 2 layer of plastic cover after installation, deep cleaning before handover . Actual laid area shall be measured and paid for this item. Make- Kajaria / Asian. Basic price - 900/ sqm . Make Epoxy Grout- Saintgobain Weber. | Tile: Kajaria / Johnson / Somany/ Asian ; Epoxy Grout, Adhesive - Weber-Saintgobain | Sqm | 100 | 1940.436 | 194043.6
8 | Vitrified tiles wall dado 600 x 600 / 300X600 | Supply and laying of 600X600mm / 300X600 mm Vitrified tiles laid over adequate thickness of cement mortar 1:4(1cement:4 coarse sand) with 2mm thk spacers filled with epoxy grout . Cost includes corner beading and ancillary works , Actual laid area shall be measured and paid for this item. Make- Kajaria / Asian. Basic price - 900/ sqm . Make Epoxy Grout- Saintgobain Weber. | Tile: Kajaria / Johnson / Somany/ Asian ; Epoxy Grout,Adhesive - Weber-Saintgobain | Sqm | 158.6 | 1940.436 | 307753.1496
9 | Cement plastering | Existing wall to be finished with 12 mm thick cement plaster in CM 1:5 to walls Internal in single coat at all levels to correct line to a maximum of 50 mm and level including scaffolding, if any, and rounding off or champhering of corners, cleaning of surface, raking out joints, chiseling the undulated surface wherever necessary and curing, etc., all materials and labour complete in all respects including all lead, lift and descent and as directed | Make- Ultratech / Ramco | Sqm | 158.6 | 477 | 75652.2
10 | Granite Ledge | Providing and fixing thresholds of 18mm thick pre-polished granite slab of approved shade fixed along the doors (it shall be provided flush with finished edges of the wall as per the wall thickness) on a bed of average 35mm thick cement mortar 1:4, as per detailed design the width 100 to 300mm and as directed and shall be provided flush with adjoining flooring levels, with all exposed edges finished as per details and with machine mirror polishing. (Basic Cost of Granite - Rs. 250/- per sq.ft) All complete as per instruction & satisfaction of Project Managers. |  | Rmt | 30 | 3029.3125 | 90879.3756
11 | Washbasin counter - Granite finish | 600 mm wide counter for wash basin in 19mm thk granite finish . Powder coated MS angle frame support to be fixed to the brick wall and covered with 18mm thk PVC integral board. 19mm thk granite to be cladded over on PVC integral board as per the detail dwg . Includes 300 mm fascia below counter and 10 mm band above counter granite finish , c . Necessary cutouts to be taken in the counter to insert wash basin and trash bin . |  | Rmt | 10 | 10070 | 100700
12 | False Ceiling - Metal | Providing & Fixing MetalWorks Lay in Perforated metal ceiling System consisting of 600mm x 600mm Lay in tiles of pre coated galvanized steel in 0.5 mm thickness in approved color with perforation of 2.5mm dia, 5.5mm square pitch & open area of 16% with Freudenberg Soundtex/ Owens Corning Acoustimax S acoustical fleece on the back of the tile to be laid on grid systems with black silhouette 15mm wide T - section flanges. The tiles should have Humidity Resistance (RH) of 95%, NRC of 0.70 (Soundtex C1986SP of Freudenberg or Acoustimax S of Owens Corning fleece inlay or as per detail drawing), Fire Performance A2-s1.d0 in module size of 600 X 600 mm, suitable for Green Building application, with Recycled content of 25%. Cross tees shall have staked XL clips that ensure a minimum pull off strength of 100 Kgs/joint. The Tile & Grid system used together should carry a 10 year warrantee. The rate should be inclusive of necessary cutouts for Services etc. Load test as per manufactures to be carried out on site and test certificate to be provided.. Make- Fameline / Daiken. Basic price - 1800 /Sqm | Daiken / Fameline | Sqm | 100 | 2332 | 233200
13 | Gypsum Ceiling | Providing & Fixing of 12.5mm thk MR Gypsum board false ceiling to G.I. framing in perfect level. Necessary offsets and grooves to be provided at the junction of ceiling & walls/columns/partitions etc., Cut out for light fittings A/C grills etc. Rate to include providing & fixing of necessary G.I./wooden/MS frame supports for the above fixtures & additional suspenders & the ceiling in AC duct area as per architects instructions. G.I.frame to consist of proprietary supplied frames & as per manufacturers recommendations suspended from dash fasteners anchored to structural slab by means of G.I.angles. Gypsum board fixed with proprietary supplied fixing devices & finished. The joint between the sheets of plasterboard are to be covered with jointing paper tape and flushed with UB 888 (all purposes jointing compound) to provide a smooth durable and professional finish. Suspension points and clips shall be able to take a minimum safe load of 50 kgs. including making grooves at the junction of ceiling & walls/columns/partitions etc. Cut-outs for light fittings, A/C grills etc. to be left wherever necessary. the ceiling profile shall be as per Architects instructions. The rate shall be inclusive of preparing the surface, providing and applying 2 coats of proper putty and primer and 3 coats of paint, roller applied Acrylic emulsion paint of approved quality / colour to Architect's approval. All complete including return air slits etc. & A/C boxing wherever indicated. Note : Marking of Electrical , Fire Alarm & Air-conditioning & co-ordination with marking of fixtures to be considered. Gypsum ceiling to be installed as per IGL specifications. Note : Marking of Electrical , Fire Alarm & Air-conditioning & co-ordination with marking of fixtures to be considered. Note: Measurement to be along the horizontal surface of the ceiling and the verticals (till 200mm ht) shall be included in arriving at cost. Rate quoted to include vertical drops (till 200mm ht) and all cut-outs required for light fixtures, smoke detectors and other services cut-outs complete as directed by Architect. Verticals above 200mm ht will be measured separately. Rate to include cove lighting provision as per detail drawings | USG / Gyproc | Sqm | 20 | 1462.8 | 29256
14 | Rest room Signage | 6 x 9 inch Restroom Sign in Stainless Steel Metal, Engraved, Door / Wall Mount Sign, Silver and Black | SS | Nos | 5 | 1537 | 7685
15 | Rest room Cubicles- Top hung cubicle - Merino / Greenlam /Stylam | Providing & fixing SS Top Hung module 12mm HPL partition with SS 304 Hardware & SS finish sections. standard dimension 1050/1200mm (Width) x1650 mm (L) X 2000mm Ht . -Thickness of Compact Laminate :12 mm Thick Size of Cubicle : Pl refer Rest room Floor plan and submit shop dwg Door Size for Cubicle : 600mm Bottom Gap - 100 mm . Cost includes taking necessary supports for the top hung cubicle from true ceiling . | Greenlam Air collction Wind / Eq in Merino / I Space | Nos | 10 | 30531.6107 | 305316.1074 | Make - Merino & Model - ZMS SS Series considered.
16 | HD - 1200 x 2400mm (For Handicap Toilet Entrance) - Sliding Door | Providing and constructing single shutter sliding door of 1200 mm size made of 38mm thick blockboard of approved make with Haffle / Hettich sliding track profile , Shutter to be finished in 1mm thk glossy laminate of approved shade, inclusive of all hardwares , Recessed SS handle , Vaccant / Engaged lock , door floor stoppr as per detailed drawing complete. (Make Fittings - Haffle / Hettich) . Blockboard : Prestige/Greenply / Century , Make of Laminate - Merino, Greenlam, Century.Basic Price - Rs- 750 / sqm . Cost includes 200X400 mm powder coated ventilation grill and laminated pelmet above sliding track . | (Make Fittings - Haffle / Hettich) . Blockboard : Prestige/Greenply / Century , Make of Laminate - Merino, Greenlam, Century.Basic Price - Rs- 750 / sqm | Nos | 1 | 59413 | 59413
17 | 1200 x 2400 mm Aluminium Door Frame & Flush door with Full Ht (Toilet) | Door Jamb : 100mm X 25mm Proprietary anodised aluminium section with black powder coated finish.. Black anodised Action : Single Swing . 100X25X2400 mm Ht . Door frame to be grouted to the PCC Floor with suitable Brackets as per manufacturers specification. Black anodised Shutter Construction : 32mm thk Flush door in laminate finish with vision panel as per detail dwg . Cost includes 200X400 mm powder coated ventilation grill . Make - Greenply / Century Hinge Type : 4 Nos Hinges . Dorma / Gaze 5" Flush suitable to style shutter Lockset : Dorma 952 Narrow style lock / GEZE 8134002 Door Handle : D Type offset handle 450 mm high . Black anodised Door Closer: - Dorma TS 71 Door Closer / Eq GEZE Door Stopper : Dorma / Geze Door frame make: Alloy / Geze / JEB Glass- Saint Gobain . | GEZE / Alloy / JEB . Glass - Saintgobain | Nos | 1 | 53689 | 53689 | Door Frame - Alloy make considered. Door Hardwares - Geze make considered.
18 | 900 x 2100 mm Aluminium Door Frame & Flush door with Full Ht Restrooms) | Door Jamb : 100mm X 25mm Proprietary anodised aluminium section with black powder coated finish.. Black anodised Action : Single Swing . 100X25X2400 mm Ht . Door frame to be grouted to the PCC Floor with suitable Brackets as per manufacturers specification. Black anodised Shutter Construction : 32mm thk Flush door in laminate finish with vision panel as per detail dwg . Cost includes 200X400 mm powder coated ventilation grill . Make - Greenply / Century Hinge Type : 4 Nos Hinges . Dorma / Gaze 5" Flush suitable to style shutter Lockset : Dorma 952 Narrow style lock / GEZE 8134002 Door Handle : D Type offset handle 450 mm high . Black anodised Door Closer: - Dorma TS 71 Door Closer / Eq GEZE Door Stopper : Dorma / geze Door frame make: Alloy / Geze / JEB Glass- Saint Gobain . | GEZE / Alloy / JEB . Glass - Saintgobain | Nos | 2 | 52629 | 105258 | Door Frame - Alloy make considered. Door Hardwares - Geze make considered.
19 | 750 x 2100 mm Aluminium Door Frame & Flush door with Full Ht (Shower room) | Door Jamb : 100mm X 25mm Proprietary anodised aluminium section with black powder coated finish.. Black anodised Action : Single Swing . 100X25X2100 mm Ht . Door frame to be grouted to the PCC Floor with suitable Brackets as per manufacturers specification. Black anodised Shutter Construction : 32mm thk Flush door in laminate finish with vision panel as per detail dwg . Cost includes 200X400 mm powder coated ventilation grill . Make - Greenply / Century Hinge Type : 4 Nos Hinges . Dorma / Gaze 5" Flush suitable to style shutter Lockset : Dorma 952 Narrow style lock / GEZE 8134002 Door Handle : D Type offset handle 450 mm high . Black anodised Door Closer: - Dorma TS 71 Door Closer / Eq GEZE Door Stopper : Dorma / Geze Alloy / Geze / JEB Glass- Saint Gobain . | GEZE / Alloy / JEB . Glass - Saintgobain | Nos | 1 | 49916.3636 | 49916.3636 | Door Frame - Alloy make considered. Door Hardwares - Geze make considered.
20 | Shaft Door | Providing and fixing Metal powder coated shaft door of size - 750 mm (W) X 1500 mm(Ht) . With Door frame , Recessed handle, Lock etc., |  | QRO-Nos |  | 25970
21 | Luster paint | Providing & applying of Luster painting for walls. Shall be applied with oil based primer coat after rubbing with sand paper onto the existing wall surface. Surface to be smoothened using chalk putty as directed. Uneven surfaces to be finished with 2 coats of chalk powder putty on the primer. Surfaces are then sandpapered to achieve a smooth surface and 3 coats of luster Paint of approved shade to be applied. The top coat should be 3 coats of 'Superfine' roller matt finish. The colour should be approved by Architect. Note : Rate should be inclusive of Masking for fixtures & wooden frames. | Asian /Dulex | Sqm | 25 | 318 | 7950
22 | Mirror | Providing and fixing of 6mm thick float mirror of approved make edge polished and without any defects, waves etc., shall be mounted on 12mm thick Marine ply (IS 710) backing with approved 3M Double sided tape / Adhesive as per details. To have aluminium U channel on Top and bottom to hold mirror as per details. Modiguard float mirror shall be considered. Rate including cove light provision and LED strip light all around mirror. | Marine ply - Archid /Century . 3M | Sqm | 10 | 4187 | 41870
23 | Wash basin counter in corian finish | 600 mm wide, 800 mm high wash basin counter made of 18mm thk WPC / PVC integral board , MS angle support finished with 12mm thk corian . Cost includes 100 mm high band above counter and 300 mm high front fascia as per detail dwg. Necessary cutout to be made in counter top to fix the counter sunk washbasins and sink . Basic price corian - 900/sqft . |  | Sqm | 3 | 23850 | 71550
24 | Vacant / non Vacant Knob | Providing and fixing in position Vacant / non Vacant Indicator in toilets | Kich | Nos | 2 | 2650 | 5300
25 | SS Grab bar | Supply and Fixing of foldable type SS Grab bar for differently abled person toilet. | Jaquar | Nos | 1 | 1941.39 | 1941.39 | Mode - AHS-CHR-1503 - As per the query response.
26 | SS Grab bar | Supply and Fixing of fixed type SS Grab bar for differently abled person toilet. | Jaquar | Nos | 2 | 8213.94 | 16427.88
27 | Cockroach trap | Providing and fixing in position of Cockroach trap | Jaquar | Nos | 17 | 2703 | 45951 | Make : Chilli / ACO - As per the query response.
28 | Janitor storage | Providing and fixing janitor storage made of 18mm thk WPC / PVC integral board and finished with approved 1mm thk laminate . Height- 2100 mm . Depth- 450 mm. Cost includes adjustable vertical and horizontal shelves , Laminated shutters with finger groove handle , Lock etc., | Greenply / Century | sqm | 7 | 15370 | 107590
|  | TOTAL COST PER FLOOR ( EXCLUSIVE OF TAXES) |  |  |  |  | 2511037.0663

## HVAC SUMMARY
HVAC BOQ SUMMARY
S.No | Description | Supply Amount in INR | Installation Amount in INR | Total Amount INR
|  | PHASE-1 | PHASE-1
1 | HVAC LOW SIDE WORKS | 2237176 | 503202.1 | 2740378.1
2 | VAV SYSTEM | 58936 | 7367 | 66303
3 | VRF SYSTEM | 1663767.6 | 228324 | 1892091.6
| GRAND TOTAL (excluding taxes) | 3959879.6 | 738893.1 | 4698772.7

## HVAC Lowside
HVAC BOQ
S.NO | DESCRIPTION | UNIT | 1F | TOTAL QTY | IN INR |  | IN INR
[5 empty] | SUPPLY RATE | INSTALLATION RATE | SUPPLY AMOUNT | INSTALLATION AMOUNT
A | MECHANICAL SYSTEM
AIR CONDITIONING WORKS
1 | DOUBLE SKIN PLENUM for AHU's
All Sheet metal cabinet type double skin air plenum section for air handling units supplied by Developer.The plenum shall be constructed using double-skinned acoustic panels with minimum 0.6 mm thick pre-coated GSS sheet for outer skin and & minimum 0.6 mm plain GSS sheet for inner skin of the unit. All the panels shall incorporate 50 mm thick PUF insulation sandwiched in between inner & outer skin.
a | Double skin Plenum with all supports suiting to site conditions. Plenum colour shall be similar to the existing AHU. | Sqm | 25 | 25 | 3750 | 400 | 93750 | 10000
[5 empty] | 0 | 0
2 | OUTDOOR MOUNT TYPE EXHAUST FAN' S |  |  | 0 | 0 | 0
| All fans shall have minimum 70% total efficiency. |  |  |  | 0 | 0
a | 600 Cfm - 35 mm external static double skin cabinet type Inline fan with all necessary supports. (café exhaust). Fan shall be provided with in built fan regulator. Outdoor Mount type | Nos | 1 | 1 | 28090 | 1590 | 28090 | 1590
b | 300 Cfm - 10 mm external static Double skin cabinet type explosion proof fan with all necessary supports. (Battery room exhaust). | Nos | 1 | 1 | 20670 | 1590 | 20670 | 1590
c | Supply fixing testing & commissioning of Hyderogen sensor with sequential timer suitable control panel to operate Battery room exhaust fan at regular 2hrs interval fan run 5.0 minutes and when increse the Hyderagen level above 1% switch ON the fan. Controller shall have bypass mode to switch ON / OFF manually with necessary control wiring. | Nos | 1 | 1 | 58300 | 1590 | 58300 | 1590
d | 500 Cfm -15mm external static cabinet type fresh air fan with prefilter & necessary supports Outdoor Mount type | Nos | 1 | 1 | 20670 | 1590 | 20670 | 1590
e | 1300 Cfm - 15 mm external static double skin cabinet type Inline fan with all necessary supports. (Toilet exhaust). Fan shall be provided with in built fan regulator. | Nos | 2 | 2 | 58300 | 2120 | 116600 | 4240
| Note: All Exhaust, Scrubber & Fresh air units should be compatible of third party BMS system integration & fire trippig should be consider in part Electrical vendor scope. HVAC vendor should be coordinate with Electrical & BMS vendor. |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
3 | Sheet Metal Work using with Ductmate(TDF) Flanges for all sizes of the duct. Fabrication as per SMACNA Standards |  |  | 0 | 0 | 0
3.01 | Galvanizing shall be Class VIII – light coating of zinc, nominal 120 gm / sqm surface area and Lock Forming Quality prime material alongwith mill test certificates. In addition, if deemed necessary, samples of raw material, selected at random by owner’s site representative shall be subject to approval and tested for thickness and zinc coating at contractor’s expense. |  |  | 0 | 0 | 0
| All duct construction and installation shall be in accordance with SMACNA standards. In addition ducts shall be factory fabricated utilizing the following machines to provide the requisite quality of ducts. |  |  | 0 | 0 | 0
| All ducts shall be fabricated and installed in workmanlike manner, conforming to relevant SMACNA codes. |  |  | 0 | 0 | 0
| Above 1000mm width duct bends Vanes to be considered every 300mm once cost inclusive of this items. |  |  | 0 | 0 | 0
| The Duct shall be supported with specified Supports at regular intervalas as mentioned in the technical specifications. (To ensure the air tightness, (All ducts shall be checked with third party Pressure test after completion of installation but before applying insulation) Report should be submit |  |  | 0 | 0 | 0
| Rectangular ducting |  |  | 0 | 0 | 0
| Sheet Metal Ducting As per Specification. Pressure 500 Pa |  |  | 0 | 0 | 0
a | 26 G Ducting with TDF flanges(0-550mm) | Sqm | 340 | 340 | 750 | 159 | 255000 | 54060
b | 24 G Ducting with TDF flanges(551-900mm) | Sqm | 150 | 150 | 875 | 159 | 131250 | 23850
c | 22 G Ducting with TDF flanges(901-1200mm) | Sqm | 75 | 75 | 975 | 159 | 73125 | 11925
d | 20 G Ducting with TDF flanges(1201-1600mm) | Sqm | 10 | 10 | 1100 | 159 | 11000 | 1590
e | 18 G Ducting with TDF flanges(1601 & above) | Sqm | 15 | 15 | 1325 | 159 | 19875 | 2385
3.02 | Supply & applying of spray painting for exposed rectangular ducts(colour to confirmed by PMC/ARCH) -2 coats of primer to be considered as first level. Further based on finalized color one set of painting to be done. And final coat to be applied | Sqmt |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
3.04 | ELLIPTICAL DUCT |  |  |  | 0 | 0
| Supply and installations of factory made Sheet metal Flat oval Spiral ducting with (factory made internal thermal insulation -9 mm thick closed cell material to be considered cost of this shall be inclusive of this item) fittings, Wire supports, The factor of wire to suit to duct weight, with necessary anchor fasteners and hook arrangements with suitable rod thickness,etc., confirming SMACNA standards. Duct should be fabricated by using CNC machines, Including necessary civil works as per site condition. Exposed ducts color to match interior requirement. Colour shall be confirmed by Architect. The joints shall be 100% leak proof. The duct should be factory made internally insulated with 9mm thick antimicrobial nitrile rubber. (Light test need to considered for elliptical ducts) |  |  |  | 0 | 0
a | 24 G ( With Ductmate Flanges) | Sqm | 25 | 25 | 1060 | 212 | 26500 | 5300
b | 22 G ( With Ductmate Flanges) | Sqm | 30 | 30 | 1219 | 212 | 36570 | 6360
c | 20 G (With Ductmate Flanges) | Sqm | 10 | 10 | 1378 | 212 | 13780 | 2120
d | 18 G (With Ductmate Flanges) | Sqm |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0
4 | Air Terminal Devices |  |  | 0 | 0 | 0 | 0 | 0
4.01 | Linear Slot Diffusers - to be fixed in techzone ceiling |  |  |  | 0 | 0
| Adjustable curved slot diffuser with aesthetically shaped face section, suitable for installation in false ceiling system. Comprising face section with 1-4 slots, either with integral or additional slide on flanges, end caps (plates or angles) and with inset air control blades which can be used to provide any direction of air discharge. These blades are factory set but can be site adjusted by others to alter air discharge direction to meet local requirements. Complete with rear mounted plenum box fitted with side entry spigot and four suspension brackets to hang complete assembly from the ceiling. The slot diffuser has a variable neck length and depending on construction, the diffuser face section can be factory fitted to the plenum box or suplied superately for second fix on site. (colour to be confirmed by Architect before placing the order. |  |  |  | 0 | 0
| 3- Slot Linear Diffuser (16 mm wide Slot) - 150 mm wide |  |  |  | 0 | 0
a | Slot Diffuser as per specification but without plenum box & End Flanges | RMT | 10 | 10 | 1484 | 212 | 14840 | 2120
b | End Flanges suitable for above size | Set | 2 | 2 | 477 | 132.5 | 954 | 265
c | Hit & Miss Damper for above size | Sqm | 1 | 1 | 3710 | 371 | 3710 | 371
[5 empty] | 0 | 0
4.02 | Circular Diffusers (with out collar damper) |  |  |  | 0 | 0
| Powder coated, extruded aluminium, removable center core type, supply / return air diffusers without volume control dampers of aluminium construction of the following neck sizes. The diffuser shall be mounted in the GI box (not in scope), with inlet connector suitable for flexible duct. GI Box & Flexible duct quantified seperately. Measurement shall be based on outer to outer size of the air terminal device ( colour for the grill to b confirmed by Arch/ PMC team before placing the order) |  |  |  | 0 | 0
| 250mm dia | Nos | 1 | 1 | 1378 | 212 | 1378 | 212
| 315mm dia | Nos | 1 | 1 | 1484 | 212 | 1484 | 212
[5 empty] | 0 | 0
4.03 | Circular Diffusers (with collar damper) |  |  |  | 0 | 0
| Powder coated, extruded aluminium, removable center core type, supply / return air diffusers without volume control dampers of aluminium construction of the following neck sizes.Measurement shall be based on outer to outer size of the air terminal device (colour for the grill to b confirmed by Arch/ PMC team before placing the order) |  |  |  | 0 | 0
| 250mm dia | Nos | 1 | 1 | 1696 | 212 | 1696 | 212
| 315mm dia | Nos | 15 | 15 | 1908 | 212 | 28620 | 3180
[5 empty] | 0 | 0
4.04 | Powder coated, extruded aluminium, removable center core type, square tegular type diffusers of aluminium construction of the following neck sizes. The diffuser shall be mounted in the GI box (not in scope), with inlet connector suitable for flexible duct. GI Box & Flexible duct quantified seperately. ( colour to be confirmed by Arch/ PMC team before placing the order) |  |  | 0 | 0 | 0 | 0 | 0
| (All are of 600 x 600 MM Outer to Outer Size) |  |  | 0 | 0 | 0 | 0 | 0
a | 450 x 450 MM (Neck Size) | Nos | 30 | 30 | 1590 | 212 | 47700 | 6360
b | 375 x 375 MM (Neck Size) | Nos | 80 | 80 | 1484 | 212 | 118720 | 16960
c | 300 x 300 MM (Neck Size) | Nos | 5 | 5 | 1431 | 212 | 7155 | 1060
|  |  |  | 0 | 0 | 0 | 0 | 0
4.05 | Powder Coated grilles for supply and return distribution ( colour for the grill to b confirmed by Arch/ PMC team before placing the order) . Deflection of the grille shall be 0 / 15 / 30. same will be confirmed later. Single / 2 way / 4 way deflection shall be confirmed later. | Sqm | 2 | 2 | 5035 | 1272 | 10070 | 2544
4.06 | Collar Dampers of opposed blade type made out of Aluminium alloy extrusion with anodised matt black finish (quantity including for diffusers & grills) | Sqm | 1 | 1 | 6148 | 1272 | 6148 | 1272
4.07 | Powder Coated Curved grilles with collar damper for supply distribution in Oval duct ( colour for the grill to b confirmed by Arch/ PMC team before placing the order) . Deflection of the grille shall be 0 / 15 / 30. same will be confirmed later. | Sqm | 1 | 1 | 15900 | 1272 | 15900 | 1272
|  |  |  | 0 | 0 | 0 | 0 | 0
4.08 | Volume Control Dampers made out of 100 x 40 x 1.55 mm thick galavanised steel frame and blades of 1.55 mm galavanised sheet steel. For Rectangular & elliptical duct. | Sqm | 5 | 5 | 6095 | 1272 | 30475 | 6360
|  |  |  | 0 | 0 | 0 | 0 | 0
4.09 | Motorised On/off type volume Control Dampers made out of 100 x 40 x 1.55 mm thick galavanised steel frame and blades of 1.55 mm galavanised sheet steel | Sqm | QRO | 0 | 0 | 0 | 0 | 0
4.1 | Actuators with control panel, panel should be compatible for third party BMS integration .necessary fire integrator should be consider in part HVA Cvendor scope | Nos | QRO | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
4.11 | Motorized Modulating type low leakage air dampers for fresh air modulation with actuator complete with all accessories like Actuator,control panel etc and any necessary requirement which can perform the controlling the Damper. It shall be integrated with Co2 sensor and based on CO2 levels, damper shall be modulate. | SQM | QRO | 0 | 0 | 0 | 0 | 0
4.12 | Supply & fixing of CO2 sensor for above fresh air same should be integrate with BMS system. | NOS | QRO | 0 | 0 | 0 | 0 | 0
4.13 | ACTUATORS with control panel should be compatible for third party BMS integration .necessary fire integrator should be consider in part HVACvendor scope | NOS | QRO | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
4.14 | Insulated Flexible Ducting |  |  | 0 | 0 | 0 | 0 | 0
| Factory Fabricated Insulated Flexible made out aluminium for connecting from main duct to diffuser box. The length of the flexible duct shall be around 1.0 to 1.5 mtr |  |  | 0 | 0 | 0 | 0 | 0
| The flexible duct shall me made of double lamination of aluminium foil, polyester and metalised polyester film permanently bonded to a coated spring steel wire helix. The exterior shal be wrapped with 25mm thick 16 kg / cum fibreglass insulation. The outer insulation jacket / vapour barrier made of fibreglass reinforced metalised polyester film laminate. (jubilee clamp at both end need to provide) |  |  | 0 | 0 | 0 | 0 | 0
a | 150 mm dia ( uninsulated flexible duct) | Rmt |  | 0 | 0 | 0 | 0 | 0
b | 200 mm dia | Rmt | 10 | 10 | 371 | 143.1 | 3710 | 1431
c | 250 mm dia | Rmt | 75 | 75 | 424 | 143.1 | 31800 | 10732.5
d | 300 mm dia | Rmt | 25 | 25 | 487.6 | 143.1 | 12190 | 3577.5
e | 350 mm dia | Rmt |  | 0 | 0 | 0 | 0 | 0
f | 150 mm dia uninsulated flexible duct | Rmt | 50 | 50 | 667.8 | 143.1 | 33390 | 7155
4.15 | Butterfly Dampers-22 Guage |  |  | 0 | 0 | 0 | 0 | 0
a | 150 mm dia | Nos | 25 | 25 | 583 | 143.1 | 14575 | 3577.5
b | 200 mm dia | Nos | 5 | 5 | 689 | 143.1 | 3445 | 715.5
c | 250 mm dia | Nos | 45 | 45 | 795 | 143.1 | 35775 | 6439.5
d | 300 mm dia | Nos | 15 | 15 | 901 | 143.1 | 13515 | 2146.5
e | 350 mm dia | Nos |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
4.16 | Rigid round ducts fabricated out of 22 G sheets to be used as extention pieces at the diffuser boxes. |  |  | 0 | 0 | 0 | 0 | 0
a | 250mm dia | Rmt | 25 | 25 | 848 | 106 | 21200 | 2650
b | 300mm dia | Rmt | 5 | 5 | 1007 | 106 | 5035 | 530
|  |  |  | 0 | 0 | 0 | 0 | 0
4.17 | SPILL AIR BOXES |  |  | 0 | 0 | 0 | 0 | 0
a | Supply,installation,testing & comissioning of 525 x 525 x 450 mm High Sheet Metal Spill air boxes made out of 26 GI sheet for connecting the diffuser outlet & flexible connection from the main duct. (10 mm internal acoustic insullation to be provided) cost inclusive of the item | Nos | 45 | 45 | 1961 | 212 | 88245 | 9540
b | Supply,installation,testing & comissioning of 1200 x 150 x 450x250dia mm High Sheet Metal Spill air boxes made out of 26 GI sheet for connecting the diffuser outlet & flexible connection from the main duct.(10 mm internal acoustic insullation to be provided) cost inclusive of the item | Nos | 1 | 1 | 2544 | 212 | 2544 | 212
b | Supply,installation,testing & comissioning of 300 x 300 x 450mm High Sheet Metal Spill air boxes made out of 26 GI sheet for connecting the diffuser outlet & flexible connection from the main duct.(10 mm internal acoustic insullation to be provided) cost inclusive of the item | Nos |  | 0 | 0 | 0 | 0 | 0
c | Supply,installation,testing & comissioning of 600 x 150 x 450 mm High Sheet Metal Spill air boxes made out of 26 GI sheet for connecting the diffuser outlet & flexible connection from the main duct. | Nos | 10 | 10 | 1961 | 212 | 19610 | 2120
[5 empty] | 0 | 0 | 0 | 0
5 | Fire Sealent: Make: Hilit/3M |  |  | 0 | 0 | 0 | 0 | 0
a | Supply and installation of Acrylic fire stop sealant CP606 or Approved Equivalent )with minimum 2 hours fire rating when tested in accordance with UL 1479 standards, shall be used along the periphery of ducts & chiller pipes without insulation passing through fire rated walls and floors made of concrete, masonry, metal, gypsum construction to provide up to 2 hours insulation and integrity when subject to the test conditions of UL 1479 standards. The product shall also be age tested as per DafStb guidelines. Sealant to provide sufficient MAF, water and gas tight seal apart from providing an airborne sound transmission reduction (STC of 50) and shall be tested as per DIN 52210 for sound insulation . The product should be tested for mold resistance rating of 0 as determined by ASTM G21-96 and should have a VOC content of approx. 75 g/l as per LEED 2009. The sealant shall be FM approved. All installations to be in full accordance with the manufacturer. The sealant should be tested in accordance with IEC 60068-2-57:1999-11 (Environmental Testing) as per Part 2-57: Test for Vibration-Time-history method and VERTEQII for seismic zone 4. The product shall bear the UL and FM approval logo on the packing where applicable. The rate shall include the mineral wool backing material and other miscellaneous items etc.., Assumed 15% Penetrants Ocupancy. Firestop installation should be done by HAFSC ( Accredated Firestop Speciality Contractor by providing complete installation report using CFS DM). Or using FIT (Firestop Installer Training) Program. As per IFC Guideliness EJ is recomended for non standard openings.-( supply & return air ducts.) | Sqm | 2 | 2 | 6201 | 1330.3 | 12402 | 2660.6
|  |  |  | 0 | 0 | 0 | 0 | 0
6 | Fire dampers CBRI APPROVED for AHU supply & return air ducts.16 Guage -frame & 16 Guage Blade to be considered.Interlocking of fire dampers using copper control wiring and requisite relays with existing AHU starter panel shall be affected as required. The dampers shall be BMS compatible as per the specifications. Damper shall be Multi-blade type damper with 2.0 hours fire rating | Sqm | 5 | 5 | 13780 | 1431 | 68900 | 7155
6.1 | Actuators with Control Panel for above fire dampers- HIGH TORQUE TYPE-10/15 NM (Actuators shall be spring return type. 24 / 230 VAC) Panel should be compatible for third party BMS integration .necessary fire integrator should be consider in part HVACvendor scope | Nos | 4 | 4 | 12720 | 1431 | 50880 | 5724
6.2 | Actuators with Control Panel for critical room fire dampers- MEDIUM TORQUE TYPE 5 NM (Actuators shall be spring return type. 24 / 230 VAC) Panel should be compatible for third party BMS integration .necessary fire integrator should be consider in part HVACvendor scope | Nos | 3 | 3 | 10070 | 530 | 30210 | 1590
|  |  |  | 0 | 0 | 0 | 0 | 0
6.3 | Supply, installation, testing and commissioning of Fusible link type Fire Damper of 90 minutes fire resistant complete with all standard accessories. Fire damper as per UL 555-S, outer shell constructed with 1.6mm thick galvanized steel frame and the blade/Leaf with 1.6mm thick GSS in accordance with the GFC/ shop drawings | Sqm | 0.5 | 0.5 | 15900 | 1431 | 7950 | 715.5
|  |  |  | 0 | 0 | 0 | 0 | 0
7 | CABLES and END TERMINATIONS. |  |  | 0 | 0 | 0 | 0 | 0
| Supply, laying, testing & commissioning of MS insulated MS sheathed, steel armoured ,aluminium conductors 1100 V grade power cables. The cables shall be laid in tray built up trench etc., Rate shall exclude the cost of tray |  |  | 0 | 0 | 0 | 0 | 0
a | 3 runs of 2.5 sq.mm HFLS Cu Wire in 19 mm dia MS Conduit for damper panel to Fire dampers | Rmt | 100 | 100 | 265 | 63.6 | 26500 | 6360
b | 3 runs of 2.5 sq.mm HFLS Cu Wire in 19 mm dia MS Conduit for AHU panel to Fire damper | Rmt | 100 | 100 | 265 | 63.6 | 26500 | 6360
|  |  |  | 0 | 0 | 0 | 0 | 0
8 | Supply Fabrication , and erection of Double canvas connection made out of fire retardent canvas cloth with Zip required necessary fixing arrangements including nuts & bolts Etc | Sqm | 5 | 5 | 1272 | 318 | 6360 | 1590
|  |  |  | 0 | 0 | 0 | 0 | 0
9 | DUCT INSULATION MATERIALS |  |  | 0 | 0 | 0 | 0 | 0
9.01 | Supply and installation of (Accoustic) Duct liner (Insulation) of specified thickness of Elastromeric Rubber Insulation manafactured as per ASTM E 84 test & which should also meet NFPA 90A supplementary materials for air distribution system which should not absorbs less 0.2% water by volume (ASTM c 209), should not support microbial growth (ASTM C1071, G21, G22) and should emit objectionable odors (ASTM C 665) and should have thermal conductivity of 0.27 ( R - 2.78 in 3.4" thickness) and water vapor permeance of 0.10. - Class "1" Material-.All joints of the Insulation material should be further covered with 50 mm wide 3 mm thick self adhesive tape made of similar material & Black Cotton Tape shall not be used. FM APPROVED |  |  | 0 | 0 | 0 | 0 | 0
a | 10 mm thick- | Sqm | 50 | 50 | 742 | 159 | 37100 | 7950
b | 13 mm thick With aluminium foil | Sqm |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
9.02 | Supply and installation Thermal (Insulation) of specified thickness of Elastomeric Rubber Insulation manufactured as per ASTM E 84 test & which should also meet NFPA 90A supplementary materials for air distribution system which should not absorbs less 0.2% water by volume (ASTM c 209), should not support microbial growth (ASTM C1071, G21, G22) and should emit objectionable odors (ASTM C 665) and should have thermal conductivity of 0.27 ( R - 2.78 in 3.4" thickness) and water vapor permeance of 0.10. Joints should be sealed with 100 mm wide 3mm thick self adhesive tape (Black Cotton Tape not acceptable). Class "O" Material-Material should be FM approved. For internal ducts ,insulation should be provided without any patches . For under deck insulation, surface should be dust free .One coat adhesive to be provide on surface & material should be provided.(Green color) |  |  | 0 | 0 | 0 | 0 | 0
a | 9 mm thick | Sqm | 600 | 600 | 265 | 137.8 | 159000 | 82680
b | 13 mm thick With aluminium foil | Sqm |  | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
9.03 | AHU Room walls where ever indicated as per the drawings to be acoustically lined with 50 mm thick factory fabricated fibre glass 32 kg/m3 denstiy acoustic panels of 1200 x 1200 mm or 600 x 600 mm in size. Air Gap of 50 mm to be provided behind the panels as shown in the drawings | Sqm | 75 | 75 | 1908 | 212 | 143100 | 15900
|  |  |  | 0 | 0 | 0 | 0 | 0
10 | Sound Attenuators (for supply and return air ducts) |  |  | 0 | 0 | 0 | 0 | 0
| Sound attenuator qty shall be measured on cross section and not on the surface area |  |  | 0 | 0 | 0 | 0 | 0
| COMPUTER SELECTION SHOULD BE ATTACHED |  |  | 0 | 0 | 0 | 0 | 0
| Sound Attenuators of dissipative type to be provided on the supply & Return air duct entering the AHU Room. |  |  | 0 | 0 | 0 | 0 | 0
| Sound Attenuators shall consist of outer casing, sound absorbing material and internal baffles, splitters and supports as expalined in the technical specifications. |  |  | 0 | 0 | 0 | 0 | 0
| Casing shall be of galavanised steel of not less than 20G in thickness. Casings shall be tested to 150mmwg and shall show no leakage or distortion in this condition. |  |  | 0 | 0 | 0 | 0 | 0
| Sound absorbing material shall be high density fibre glass held in place with at least 5% compression to prevent voids due to settling. Absorption material density shall be minimum 48 kg/cum. Fibreglass faced with minimum 26 g perforated galvanised sheet metal of minimum 40% open area. Combustion ratings shall be as expalined in the tender specifications |  |  | 0 | 0 | 0 | 0 | 0
a | Supply,Installation & commissioning | Sqm | 5 | 5 | 7208 | 1272 | 36040 | 6360
[5 empty] | 0 | 0
b | Acoustic Louvers (Z Pieces) - to be installed for all rooms & closed cabins |  |  |  | 0 | 0 | 0 | 0
| Sound attenuator qty shall be measured on surface area |  |  |  | 0 | 0
| Supply and installation of RA intake with acoustic duct Z pieces of 450 / 600 / 900 mm length to suit site requirements & as shown on the approved drawing complete with: |  |  |  | 0 | 0
| a) Sheet steel enclosure |  |  |  | 0 | 0
| b) Acoustic Z piece duct (inside of duct sheets with both sides lining & a centre baffle sheet also lined on both sides with 15 mm thk Armasound Nitrile acoustic insulation- with Thermal conductivity 0.045 W/m deg.K / density 140~180 kg/m3, with manufacturer recommended adhesive 520 bonding. |  |  |  | 0 | 0
| c) Z piece sample to be approved at site beforehand. | Sqm | 30 | 30 | 2650 | 371 | 79500 | 11130
[5 empty] | 0 | 0
11 | SEQUENTIAL CONTROL PANNEL |  |  | 0 | 0 | 0 | 0 | 0
| Supply installation , testing & commissioning of sequential control panel all necessary supporting materials |  |  |  | 0 | 0
| Auto sequnetial controller for UPS and Battery rooms (it shall be with timer control as well as temperature based operational sequence). Temperature sensor shall be provided with digital display on the panel |  |  | 0 | 0 | 0 | 0 | 0
| A/C units should be able to restart automatically after power failure/Interruption |  |  | 0 | 0 | 0 | 0 | 0
| Automatic fault chnageover based on AHU operation, when Ahu ON both the VRF indoor unit will be switch OFF, and when AHU is switched OFF automatically switch ON the VRF unit and operated based on sequece basis with necessary controller and cable's considered from VRF indoor unit to AHU starter panel. Supply and return air MVCD will be open and closed based respective unit operation. |  |  | 0 | 0 | 0 | 0 | 0
| Automatic fault chnageover in case working unit fault. |  |  |  | 0 | 0
| Sequential changeover of operating units with specified timings |  |  | 0 | 0 | 0 | 0 | 0
| Monitoring of high and low temperature conditions |  |  | 0 | 0 | 0 | 0 | 0
| The panel should be provided with potential free contact for fire integration |  |  | 0 | 0 | 0 | 0 | 0
| it Should generate an alarm if the unit trips or the room temperature goes beyond the set point ,power fail,HP,LP trip |  |  | 0 | 0 | 0 | 0 | 0
| Panel should be SMS module option |  |  | 0 | 0 | 0 | 0 | 0
| Panel should be compatible for 2 Nos of MCB's status |  |  | 0 | 0 | 0 | 0 | 0
| It should give Alarm in form of audible buzzer and indication light and SMS |  |  | 0 | 0 | 0 | 0 | 0
| This controller should monitor low pressure and high pressure of Units |  |  | 0 | 0 | 0 | 0 | 0
| Control cabling of 50 mtr to be considered fror each controller. |  |  | 0 | 0 | 0 | 0 | 0
| All units should be compatible for third party BMS integration .necessary fire integrator should be consider in part HVACvendor scope |  |  | 0 | 0 | 0 | 0 | 0
| Unit configuration & No of unit to be follow as per approved shop drawing | NOS | 2 | 2 | 24910 | 1590 | 49820 | 3180
[5 empty] | 0 | 0
12 | Associated Civil Works |  |  | 0 | 0 | 0 | 0 | 0
a | Pedestals : Providing & Laying of Reinforced cement concrete of M20 grade at the level given below, using river sand, 20 mm as down size coarse aggregates, application of necessary admixtures as specified by consultants inclding all leads and lifst, scaffolding wheever necessary, curing as directed, including the cost of shuttering, centering and staging for required height. | cum |  | 0 | 0 | 0 | 0 | 0
b | Chipping, chassing & Plastering the wall openings in cement mortor 1:6 of 15 mm thick finishing to line and level with sand faced finshing at all levels, including all leads & lifts, scaffolding, curing etc complete (for SA & RA openings in ahu rooms, opgs for CHW pipes etc) | sqm | 10 | 10 | 2385 | 795 | 23850 | 7950
|  |  |  | 0 | 0 | 0 | 0 | 0
13 | AIR BALANCING WORKS |  |  | 0 | 0 | 0 | 0 | 0
| Third party Air balancing as per the approved shop drawing using valid calibrated instruments, including Air Flow HOOD which has capability to measure volumetric flow rate with digital manometer, multi point averaging air flow sensor, airflow measurement station. Documentation ,representation & Carrying on Air balancing using digital HOOD. Cost including of applying Sealent/Tightening of duct joints to reduce the air leakages with necessary tool to be considered. | Lot | 1 | 1 | 0 | 61480 | 0 | 61480
|  |  |  | 0 | 0 | 0 | 0 | 0
14 | IAQ TESTING |  |  | 0 | 0 | 0 | 0 | 0
| Indoor Air quality test to be conducted after refurbishment works considering below parameters |  |  | 0 | 0 | 0 | 0 | 0
| Inside Temperature & RH, Air movement velocity, CO2 levels, Suspended Particulate Matter Microgram /M3) (Pm 2.5 & Pm 10), Total VOC content, Formaldehyde, Nitrogen dioxide content, Ammonia content, Sulphur Dioxide content, Oxygen (O2), Bacterial and Fungal count, Hydrogen Sulfide (H2S), Ammonia (NH3), Carbon Monoxide (CO), Ozone (O3) |  |  | 0 | 0 | 0 | 0 | 0
| Total 4 points - 1 points in Board Room, 1 in Meeting room and 2 in open office area with sampling at each location 4 times during the day | Lot | 1 | 1 | 0 | 53000 | 0 | 53000
|  |  |  | 0 |  |  | 0 | 0
| GRAND TOTAL EXCLUDING TAXES | [5 empty] | 2237176 | 503202.1

## VAV
VAF SYSTEM BOQ
S.NO | DESCRIPTION | UNIT | 1F | Total Qty | IN INR |  | IN INR
[5 empty] | SUPPLY RATE | INSTALLATION RATE | SUPPLY AMOUNT | INSTALLATION AMOUNT
I | Supply , Installation,testing & commsitioning of following including frieght, local transportation upto site , handing over
VARIABLE AIR VOLUME BOXES (Damper Actuator Type)
1 | Supply , Installation,testing & commsitioning Variable Air Volume (VAV) Units are fabricated out of heavy gauge steel, mechanically sealed with gasketed & leak resistance construction. Both supply & discharge shall be suitable for duct connections. VAV Boxes Shall be self addressable type. Temperature sensor for the Cabins should be provided with selector swtich which has a selection range from 18 deg C till 30 deg C & for workstations / open office areas, it shall be thermostat without any selector switch
Boxes shall be of variable air volume at the inlet and variable at outlet and shall be fitted with air volume regulator of the fully proportional type.
The boxes shall be supplied with all internal attenuation treatment and acoustical damped casing necessary to achieve the required noise criteria. Casing shall be 20 BG minimum fitted with a completely sealed, easily removable means of access to all internal parts. Access to all boxes must be from the underside only.
Maximum allowable static pressure to the boxes for its satisfactory operation shall not exceed 0.20” WG
Boxes shall be able to reset any air flow between zero and the maximum air quantity that the boxes can handle without changing orifices or other parts. Air quantity limiters will not be accepted.
A suitable device shall be provided for the field adjustment of minimum air flow. All boxes shall be intially factory set at minimum air quantity of 50% of the design requirements. Under shut-off conditions, all boxes shall not have air leakage more than 20% of the maximum air quantity.
VAV Unit shall be ceiling suspended with hanger brackets & vibration isolators.
All accessories listed under specifications should be considered for pricing VAVs
Direct Output temperature sensor comprising of high quality thermistor or platinum sensing element should be supplied with VAVs.
The look of the sensor should be rectangular in shape as shown in our schedule drawings showing vav box quantities. Projection of the sensor should not exceed 27 mm .
Necessary Hardware/ software for integrating the VAV Boxes to the third party system which shall be capable of transferring 4 points as specified in the technical specification for the quantity indicated below shall also be considered in the scope. BAcent protocol to be considered for VAV centralized integrator and cost of the same to be inclusive
All thermostats shall be digital type.
Cat 6 - Communication cable between VAV and thermostat to be considered along with 19 mm dia PVC conduits @ 12 mtr per VAV as part of this scope. Flexible conduits of 19 mm dia to be considered for either end conection
In Open ceiling area powder coated tray support to be provided from ceiling 600mm for thermostat fixing coordinate with PMC before installations with necessary supporting materials.
1.1 | Rectangular/Elliptical Unit shall be of the following sizes : Cost shold be quote accordinling as per tender drawing
a | 0-250 CFM
| Supply & Installation of VAV boxes | Nos |  | 0 |  |  | 0 | 0
b | 251-500 CFM
| Supply & Installation of VAV boxes | Nos | 1 | 1 | 22790 | 1961 | 22790 | 1961
[5 empty] | 0 | 0
c | 501-750 CFM |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
d | 751-1000Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
e | 1001-1250Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
f | 1251-1500Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
g | 1501-1750Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
h | 1751-2000Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos | 1 | 1 | 26500 | 1908 | 26500 | 1908
[5 empty] | 0 | 0
i | 2001-2250Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
j | 2251-2500Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
k | 2501-2750Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
l | 2751-3000Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
m | 3001-3250Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
n | 3251-3500Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
o | 3501-3750Cfm |  |  |  | 0 | 0
| Supply & Installation of VAV boxes | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
s | Supply , Installation,testing & commsitioning of 2core, 1.5 Sqmm, screened ATC/sheathed cable communication cable in PVC Conduit of 19 mm dia for looping between VAV’S & BMS necessary supporting materials link clamp & screw to be considered | Rmt | 30 | 30 | 137.8 | 53 | 4134 | 1590
[5 empty] | 0 | 0
| NOTE:Looping all VAV's with communication cable & leaving the cable inside BMS room and coordinating with BMS vendor is part of HVAC vendor scope |  |  |  | 0 | 0
[5 empty] | 0 | 0
t | Suplly, installation testing & commissioning of duct pressure sensor in the rang of 0 to 500 Pascal. | Nos |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0
u | Supply, laying & Termincation of 2C X 1sq.mm copper sheiled Control cable between VFD and Duct Temperature sensor | Rmt | 20 | 20 | 137.8 | 53 | 2756 | 1060
v | Supply & fixing of 16G M.S.Conduit for cable laid between VFD and Duct Temperature sensor | Rmt | 20 | 20 | 137.8 | 42.4 | 2756 | 848
[5 empty] | 0 | 0
y | All necessary Network controller or Router, Interface to connect the proposed floor BACNET MS/TP VAV with the main BMS system via Native BACnet / IP. Network controller or Router - Shall automatic rout BACnet messages between BACnet IP, BACnet Ethernet, BACnet PTP, and BACnet MS/TP ports and sub-lan networks. It shall conformance to ANSI/ASHRAE standard 135-2008 for designated “router” functions. The controller shall support foreign device registration with BACnet Broadcast Management Devices (BBMD). Total no. of network controller shall be based on manufacturer requirement. 1 network controller / router panel shall not exceed integrating / connecting 30 VAV boxes. The Network controller or Router shall be housed in a suitable metal enclosure with proper power protection. Integrator to have necessary convertors for taking into BOS system | Nos |  | 0 | 0 | 0 | 0 | 0
Note1: VAV quantity will vary if any changes in architectural drawings
| SUB TOTAL | [5 empty] | 58936 | 7367

## VRF SYSTEM
VRF SYSTEM BOQ
SL NO | Description | Unit | 1F | TOTAL QTY | IN INR |  | IN INR |  | Remarks
[5 empty] | SUPPLY RATE | INSTALLATION RATE | SUPPLY AMOUNT | INSTALLATION AMOUNT
Supply, Installation, Testing & Commissioning & Handing over of the following:
A | VRF AIR-CONDITIONING EQUIPMENTS:(100% INVERTER TYPE ONLY TO BE QUOTED) - R410A refrigerant
1 | Supply & Installation of VRF airconditioning system comprising of Modular type high efficiency Twin Rotary Multiple Compressor with inverter, High efficiency heat transfer Cooling Coil suitable for Environment friendly R410a refrigerant,Air cooled propeller type condenser fan with DC motor drive,interconnecting piping, suction line insulation etc., Micro-processor control panel suitable for automatic operation,High speed calculation inverter control, active oil control mechanism incorporating all safety functions as per equipment specifications & other points as listed below:
The unit mounted starter panel shall be complete with IP-55 protection consisting of power disconnecting switches with fuses, soft starters, for compressor motors, under/over voltage trip, single phase preventers, communication card which can accept 4-20 mA or 2-10 Vdc analog signal.
All components shall be mounted on welded steel base frame, structural steel profiles/panels made out of galvanized sheet steel, protected with primary coat & finished with epoxy paint.
Modular type outdoor units equipped with highly efficient scroll compressors, with inverter type compressor(s),special acryl precoated heat exchanger,low noise condenser fan,auto check function for connection error, auto address & UNIT Price shall be inclusive of outdoor stand price.Shifting & Installing of ODU as per shop drawing is part VRV vendor scope.(ODU Location & Capacity mentioned below).Shifting of Out door units from GF to Terrace floor is part of VRF vendor scope
The unit shall be sized to deliver following rated capacities minimum including de-rated capacity due to ambient temperature of 36 Deg C DB
All VRV units should be compatible for third party BMS integration .necessary fire and BMS integrator should be consider in part HVAC/VRF vendor scope
1.01 | Outdoor Unit(ODU) : Cooling Capacity : 6HP SIDE/TOP DISCHARGE Based on site condition (Café) | Set | 1 | 1 | 135680 | 12720 | 135680 | 12720
1.02 | Outdoor Unit(ODU) : Cooling Capacity : 8HP SIDE/TOP DISCHARGE Based on site condition(Crtical room working) | Set | 1 | 1 | 174900 | 16960 | 174900 | 16960
1.03 | Outdoor Unit(ODU) : Cooling Capacity : 10HP SIDE/TOP DISCHARGE Based on site condition (critical room standby) | Set | 1 | 1 | 188680 | 21200 | 188680 | 21200
B | INDOOR UNITS |  |  |  | 0 | 0
| Indoor Unit(IDU): Cooling type : All the units should be supplied with Cordless remote control. The following Indoor unit capacities are required for each type of Room.Drycontact should be considered for Auto change over,failure status,overload sequencing etc.. |  |  |  | 0 | 0
1.04 | Serving Area: CAFETERIA 4.1 TR Ductable unit | Nos | 1 | 1 | 47170 | 6360 | 47170 | 6360
1.05 | Serving Area: UPS & BATTERY ROOM 3.0 TR Ductable unit | Nos | 2 | 2 | 40810 | 6360 | 81620 | 12720
1.06 | Serving Area: SERVER ROOM 3.0 TR Ductable unit | Nos | 2 | 2 | 40810 | 6360 | 81620 | 12720
1.07 | Serving Area: 2.0 TR Hi-wall unit | Nos | QRO | 0 | 0 | 0 | 0 | 0
1.08 | Serving Area: 1.5 TR Hi-wall unit | Nos | QRO | 0 | 0 | 0 | 0 | 0
1.09 | Serving Area: 1.0 TR Hi-wall unit | Nos | QRO | 0 | 0 | 0 | 0 | 0
1.1 | Serving Area: BMS ROOM 1.65 TR Compact cassette unit | Nos | 1 | 1 | 35722 | 3498 | 35722 | 3498
1.11 | Serving Area: 2.0 TR cassette unit | Nos | QRO | 0 | 0 | 0 | 0 | 0
1.1 | Serving Area: Visitors meeting room 1 TR Compact cassette unit | Nos | 1 | 1 | 33708 | 3498 | 33708 | 3498
[5 empty] | 0 | 0
C | REFRIGERANT PIPING |  |  |  | 0 | 0
1.12 | Interconnecting copper refrigerant pipe work duly insulated with elastomeric nitrile rubber type tubular insulation between indoor & outdoor units as per specifications . All piping inside the room shall be properly supported with hanger and all piping should be run in perforated cably tray.Cable tray qty specified seperately.. MS supports for refrigerant piping & cables, using angles, channels, Tees, flats, etc should be considered as part of scope.All MS supports shall be given a coat of red-oxide primer and two coats of synthetic enamel paint of approved colour. |  |  |  | 0 | 0 |  |  | Quantity updated as per builder input ODU located at terrace level.
| 41.3mm OD (insulation =19 mm thick) | Rmt |  | 0 | 0 | 0 | 0 | 0
| 34.3mm OD (insulation =19 mm thick) | Rmt |  | 0 | 0 | 0 | 0 | 0
| 28.6mm OD (insulation =19 mm thick) | Rmt | 5 | 5 | 1272 | 106 | 6360 | 530
| 22.2mm OD (insulation =13 mm thick) | Rmt | 75 | 75 | 954 | 106 | 71550 | 7950
| 19.1mm OD (insulation =13 mm thick) | Rmt | 150 | 150 | 750 | 106 | 112500 | 15900
| 15.9mm OD (insulation =13 mm thick) | Rmt | 50 | 50 | 600 | 106 | 30000 | 5300
| 12.7mm OD (insulation =13 mm thick) | Rmt | 60 | 60 | 500 | 106 | 30000 | 6360
| 9.5mm OD (insulation =13 mm thick) | Rmt | 280 | 280 | 400 | 106 | 112000 | 29680
| 6.4mm OD (insulation =13 mm thick) | Rmt | 10 | 10 | 300 | 106 | 3000 | 1060
D | DRAIN PIPE |  |  |  | 0 | 0
1.13 | Insulated Condensate Drain Piping |  |  |  | 0 | 0
| Supply Insulated PVC Condensate Drain piping as per specification as mentioned in the document insulated same as chilled water piping but without polyshield covering.Consider drip pans with drian pipe .Entire draine pipe needs to be insulated with Nitrile rubber. |  |  |  | 0 | 0
| 40 mm dia | Rmt | 20 | 20 | 450.5 | 53 | 9010 | 1060
| 32 mm dia | Rmt | 35 | 35 | 392.2 | 53 | 13727 | 1855
| 25 mm dia | Rmt | 20 | 20 | 339.2 | 53 | 6784 | 1060
1.14 | Electrical Cable between Isolator to ODU.Suitable size copper flexible cable with necessary earthing insulation | Rmt | 30 | 30 | 265 | 53 | 7950 | 1590
1.15 | Providing & fixing of 2 Cx 1.5 sqmm cu. cable for control cum trans-mission between Indoor unit and Out Door Unit through PVC Conduit. | Rmt | 330 | 330 | 118.72 | 31.8 | 39177.6 | 10494 | Quantity updated as per builder input ODU located at terrace level.
| Note:Cable from Electrical panel to isolator excluded in VRV vendor scope.same should capture in Electrical vendor scope. Cable from Isolator to ODU is part of VRV Vendorscope. |  |  |  | 0 | 0
1.16 | Imported fittings like Y-Joints and headers etc as per the layout( additional supports should consider for both ends of the Y joint) | Nos | 4 | 4 | 5406 | 530 | 21624 | 2120
[5 empty] | 0 | 0
1.17 | Supply & providing of MS stand for VRV ODU along with proper supports-suitable for above configuration | Set | 3 | 3 | 15900 | 1590 | 47700 | 4770
[5 empty] | 0 | 0
1.18 | Filling, testing, commissioning including topping up of R410 A Refrigerant. | Kg | 35 | 35 | 901 | 106 | 31535 | 3710 | Quantity updated as per builder input ODU located at terrace level.
[5 empty] | 0 | 0
E | CABLE TRAY |  |  |  | 0 | 0
1.19 | Supply & providing of GI Powder coaded cable tray (perforated type) of for routing copper pipes at terrace level. |  |  |  | 0 | 0 |  |  | Quantity updated as per builder input ODU located at terrace level.
| size:150x 50mm(14 SWG grade)-2mm thick | Rmt | 120 | 120 | 593.6 | 143.1 | 71232 | 17172
| size:300x 100mm with cover (14 SWG grade)-2mm thick Only for Exposed & Vertical shaft area | Rmt | 90 | 90 | 1113 | 196.1 | 100170 | 17649
| size:450x 100mm with cover (14 SWG grade)-2mm thick Only for Exposed area | Rmt | 20 | 20 | 1431 | 222.6 | 28620 | 4452
| size:600x 100mm with cover (14 SWG grade)-2mm thick Only for Exposed area | Rmt |  | 0 | 1961 | 254.4 | 0 | 0
[5 empty] | 0 | 0
F | DRIP TRAY |  |  |  | 0 | 0
1.2 | Supply & installation,testing & comissioning of Drip Tray with inner nitrile rubber insulation with necesssary supports | Nos | 6 | 6 | 3975 | 636 | 23850 | 3816
[5 empty] | 0 | 0
G | CENTRAL CONTROLLER & REMOTE SYSTEM |  |  |  | 0 | 0
1.21 | Supply & installation,testing & comissioning of Centarl controller integrating all floor Indoor units with necessary software & spare parts | Lot | 1 | 1 | 117878 | 2120 | 117878 | 2120
[5 empty] | 0 | 0 | 0 | 0
H | DRAIN PUMP |  |  |  | 0 | 0
a | Supply installation testing & commissioning of 2 litre drain pump with all necessary supports | QRO-Nos | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 0 | 0 | 0 | 0
b | 2 Litre SS storage tank with 2 inbuilt drain pumps (1W+1S). Tank and pumps shall be housed in a tray and supported to wall/ceiling as per site conditions sholud be BMS compactabilit | Set | QRO | 0 | 0 | 0 | 0 | 0
| GRAND TOTAL EXCLUDING TAXES | [5 empty] | 1663767.6 | 228324

## HVAC-APPROVED MAKES
LIST OF APPROVED MAKES - HVAC
Sl.No | Description | Makes
1 | EAU / VAUs / Ceiling Suspended units/ AHU’s | VTS | Zeco | Flakwoods | Systemair
2 | Double Skin Plenum | Zeco | Seven star | Shree venus | Wester air dcut
3 | Sound Attenuators | Wester air dcut | Seven star | Shree venus
4 | VRF System | Daikin | Blue Star
5 | Dx-units | Daikin | Blue Star
6 | Low Noise Exhaust Fans / Kitchen Exhaust Fans / Online Fans | Green heck | Dyanair | Systemair | Kruger
7 | Combined Smoke & Fire Dampers | Green heck | Airmaster | Systemair | Cosmic | Carriyare
8 | Grilles ,diffusers & Disc valves | Air Master | Caryaire | Systemair | Cosmic | Carriyare
9 | Galvanised Sheet Steel | SAIL | Jindal | Tata
10 | MS Pipes | Jindal | Tata steel | Sail
11 | Wire support | Hilti | 3M
12 | Duct Insulation / Acoustic Lining / Under Deck Insulation / Chilled Water Pipe Insulation | Armaflex | Aeroflex | K flex
13 | VAV | JCI | Honey well | Siemens | Belimo
14 | Duct Fabrication | Sevenstar | Shree venus | Zeco | Wester air dcut | Air Q
15 | Butterfly Dampers | Airmaster | Caryaire | Systemair | Cosmic
16 | Expansion Plenums (Acoustically Lined with ARMAFLEX Insulation) fabricated using CNC Machines | Vedha duct | Airmaster | Caryaire
17 | Fire Damper Actuators with Control Panel | Belimo | Siemens | Sauter | Airtech
18 | Cable Trays | Patni | Profab | Puspak
19 | Insulated Flexible Ducting | Caryaire | Seven star | Supaflex | Uptwiga
20 | Vibration isolators | Dunlop | Resistoflex
21 | Sound attenuators | Seven star | Shree venus
22 | Drain pipe | Ashirvad | Supreme | Astral
23 | Duct Supports | Hilti | Gripple
24 | Fire sealent | Hilti | 3M
25 | Spiral duct | Sevenstar | Spiral Tubes | Karthila
26 | Acoustic insullation | UP Twiga
27 | Copper pipes | Nippon | Rajco | Mehta | Uniflow
28 | variable frequency drive | Danfoss | ABB
29 | Bipolar Ionizers | Plasma air

## ELEC_Summary
ELECTRICAL BOQ SUMMARY
Sl.No | DETAILS OF SPECIFICATION | AMOUNT in INR
|  | SUPPLY | ERECTION | Total
1 | SUPPLY & INSTALLATION OF LUMINAIRES | 2466832 | 103895.9 | 2570727.9
2 | WIRING FOR LUMINAIRES | 768584.8 | 273024.2 | 1041609
3 | POWER OUTLETS (SOCKETS) | 375464.18 | 67818.8 | 443282.98
4 | CABLING FOR POWER OUTLETS | 817960.9 | 173840 | 991800.9
5 | UNDER FLOOR CABLE MANAGEMENT SYSTEM | 227900 | 114480 | 342380
6 | UNDER FLOOR JUNCTION BOXES | 53392.2 | 23807.6 | 77199.8
7 | SECONDARY DISTRIBUTION SYSTEMS | 254203.9 | 21560.4 | 275764.3
8 | PRIMARY DISTRIBUTION SYSTEM | 761080 | 63600 | 824680
9 | POWER CABLES AND CABLE TERMINATION | 877227.38 | 325805.84 | 1203033.22
10 | CEILING CABLE MANAGEMENT SYSTEM | 291166.1 | 47779.5 | 338945.6
11 | EARTHING | 69960 | 14840 | 84800
12 | EARTH FLAT BUS | 94013.52 | 15033.98 | 109047.5
13 | SAFETY EQUIPMENTS | 4731.84 | 318 | 5049.84
14 | ASSOCIATED ACCESSORIES | 78010.7 | 19154.2 | 97164.9
15 | SHOP DRAWINGS, INSPECTION AND APPROVALS | 185000 | 5300 | 190300
| Sub total | 7325527.52 | 1270258.42 | 8595785.94
| Grand Total | 8595785.94

## ELEC
ELECTRICAL BOQ SUMMARY
Sl.No | DETAILS OF SPECIFICATION | QTY | UNIT | RATE in INR |  | AMOUNT in INR
|  |  |  | SUPPLY | ERECTION | SUPPLY | ERECTION | As per Measurement | Amount
1 | SUPPLY & INSTALLATION OF LUMINAIRES (UGR should be less than19), Warranty for LED light fixture should be 5 years. LED CCT and Luminaire Colour as per architect/client selection & CRI >80, THD <10 (CCT 4500K)
a | Supply, Installation, Testing & Commissioning of LED Suspended Continous LED Linear Profile Light. Minimum Guaranteed Technical Parameters should be: UGR <19 , System Luminous efficacy >90Lm/W, CRI >80, THD <10, SDCM<5, IP20. Wattage: ≈40W, LED CCT options: 5700/4000/3000 K. SPD should be provided with 3.5kV, Luminaire Dimension: L = 2385 mm X Width = 50 mm And its should be EXTRUDED AL Housing with Special grade low glare MPO diffuser. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions, similar to Arraystorm Lighting Model No: ASCL5285SFXXIN040-8FT | 10 | Nos | 3286 | 291.5 | 32860 | 2915 | 5 | 16430
b | Supply, Installation, Testing & Commissioning of LED Suspended Continous LED Linear Profile Light. Minimum Guaranteed Technical Parameters should be: UGR <19 , System Luminous efficacy >90Lm/W, CRI >80, THD <10, SDCM<5, IP20. Wattage: ≈20W, LED CCT options: 5700/4000/3000 K. SPD should be provided with 3.5kV, Luminaire Dimension: L = 1195 mm X Width = 50 mm And its should be EXTRUDED AL Housing with Special grade low glare MPO diffuser. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions similar to Arraystorm Lighting Model No: ASCL5285SFXXIN020-4FT | 5 | Nos | 1727.8 | 291.5 | 8639 | 1457.5 | 1 | 1727.8
c | Supply, Installation, Testing & Commissioning of LED Suspended Continous LED Linear Profile Light. Minimum Guaranteed Technical Parameters should be: UGR <19 , System Luminous efficacy >90Lm/W, CRI >80, THD <10, SDCM<5, IP20. Wattage: ≈30W, LED CCT options: 5700/4000/3000 K. SPD should be provided with 3.5kV, Luminaire Dimension: L = 1790 mm X Width = 50 mm And its should be EXTRUDED AL Housing with Special grade low glare MPO diffuser. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions similar to Arraystorm Lighting Model No: ASCL5285SFXXIN030-6FT | 0 | Nos | 5141 | 291.5 | 0 | 0 | 3 | 15423
d | Supply, Installation, Testing & Commissioning of LED Recessed /Surface Troffer Light (2X2) Luminaire with a nominal system luminous efficacy >100 Lm/W and a Luminaire Wattage ≈ 30W with Electronic driver. Also Operating voltage of 140-270V with cut off and auto restart feature @325V. Power factor should be >0.95 & THD should be <10% & CRI>80. LED CCT options: 5700/4000/3000 K. LED Life should be 50,000Hrs. The luminaire should have Special low glare MPO diffuser. "Dimension :Length = 595 mm , Width = 595mm.The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions similiar to Arraystorm Lighting Model No: ASGL2016RFXXIN030 | 115 | Nos | 1802 | 212 | 207230 | 24380 | 119 | 214438
e | Supply, Installation, Testing & Commissioning of LED Recessed /Surface Troffer Light (2X2) Luminaire with a nominal system luminous efficacy >100 Lm/W and a Luminaire Wattage ≈ 30W . Provided with Analogue dimmable driver. Also Operating voltage of 140-270V with cut off and auto restart feature @325V. Power factor should be >0.95 & THD should be <10% & CRI>80. LED CCT options: 5700/4000/3000 K. LED Life should be 50,000Hrs. The luminaire should have Special low glare MPO diffuser. "Dimension :Length = 595 mm , Width = 595mm, Height= 50mm .The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions similiar to Arraystorm Lighting Model No: ASGL2015RFXXIN030-ANA | 10 | Nos | 4558 | 212 | 45580 | 2120 | 10 | 45580
f | Switching PIR Sensors Ceiling Mount 360 degree. Recess/Surface Mounting. Micro Detection - High Sensitivity Range 10 m Dia at height of 2.5 meter ( 7 m dia Micro Sensitivity 3 m macro) and Current Capacity 10A. Digital Remote IR based Commissioning with hand held programmer for following Programmable features: OFF delay time 10 Sec - 96 hrs, photocell and power up (status of luminaires when power is applied). It shall have provision to manually override luminary ON/OFF status using hand held remote control. 5 years Standard Warranty. Reference Model No. Honeywell LS3200RF (on/off) | 18 | Nos | 3047.5 | 212 | 54855 | 3816 | 18 | 54855
g | Digital PIR Regulating presence detection sensor. Recess/Surface Mounting. Micro Detection - High Sensitivity Range 10 m Dia at height of 2.5 meter ( 7 m dia Micro Sensitivity 3 m macro) to control 10A lighting load . Capable of dimming 15 dimmable (1-10 V Analogue Dimmable ) ballast. To be commissioned by hand held programmer with programmable features of delay time 10sec-96 hrs, photocell and power up (status of luminaires when power is applied). It shall have provision to manually override the luminaires’ ON / OFF / regulate lighting level status using hand held remote control and wired input for One switch control (push switch) to ON / OFF / regulate the lighting level. 5 years Standard Warranty. Reference Model No. Honeywell LS3000ARF (Analogue dimmable) | 2 | Nos | 6704.5 | 212 | 13409 | 424 | 2 | 13409
h | Supply, Installation, Testing & Commissioning of LED Recessed Downlighter with a nominal system luminous efficacy of >90Lm/W and Luminaire wattage of ≈ 15W. Also Safe operating voltage 140-270V AC. Power factor should be >0.95 & THD should be <10% & CRI>80. LED CCT Options 5700/4000/3000 K. LED Life should be 50,000Hrs with 2.5KV Surge Protection. Dimension: ø = 140 mm Cutout ø = 120 mm , H=40mm. Housing should be aluminium with special low glare MPO diffuser.The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions similar to Arraystorm Lighting Model No: ASDL1003RFXXIN015 | 290 | Nos | 689 | 119.78 | 199810 | 34736.2 | 196 | 135044
i | Supply, Installation, Testing & Commissioning of LED Recessed Downlighter with a nominal system luminous efficacy of >90Lm/W and Luminaire wattage of ≈ 15W. Provided with Analogue dimmable driver. Also Safe operating voltage 140-270V AC. Power factor should be >0.95 & THD should be <10% & CRI>80. LED CCT Options 5700/4000/3000 K. LED Life should be 50,000Hrs with 2.5KV Surge Protection. Dimension: ø = 140 mm Cutout ø = 120 mm , H=40mm. Housing should be aluminium with special low glare MPO diffuser.The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions similar to Arraystorm Lighting Model No: ASDL1003RFXXIN015-ANA | 5 | Nos | 3445 | 119.78 | 17225 | 598.9 | 0 | 0
j | Supplying, erecting, connecting and commissioning of 1 x 5watts per Mtrs 24V LED light fitting of approved make with necessary standard accessories. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions | 50 | mtrs | 477 | 119.78 | 23850 | 5989 | 50 | 23850
k | Supplying, erecting, connecting and commissioning of LED light fitting of with necessary standard accessories Continuous Profile based lighting using Extruded aluminium deep profile of 17mm width with frosted diffuser. 24V LED short pitch strip light having power of 12W and 1200lm per metre to be used inside profile neatly pasted using high quality self-adhesive tape of 3M. 24V non integral driver to be used for the LED strip light. The profile and LED Strip should be cuttable as per site requirements. also. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions | 50 | mtrs | 1038.8 | 119.78 | 51940 | 5989 | 50 | 51940
l | Supplying, erecting, connecting and commissioning of LED light fitting of with necessary standard accessories Continuous Profile based lighting using Extruded aluminium deep profile of 17mm width with frosted diffuser. 24V LED short pitch strip light having power of 12W and 1200lm per metre to be used inside profile neatly pasted using high quality self-adhesive tape of 3M. 24V non integral driver to be used for the LED strip light. The profile and LED Strip should be cuttable as per site requirements. also. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions (Weather Proof) | 10 | mtrs | 3392 | 119.78 | 33920 | 1197.8 | 10 | 33920
m | Supply, Installation, Testing & Commissioning of LED Surface/Suspended Cylindrical Downlighter with a nominal system luminous efficacy >90Lm/W and Luminaire wattage ≈ 15W. Also Safe operating voltage 140-270V AC. Power factor should be >0.95 & THD should be <10% & CRI>80. SPD Should be 2.5KV Surge Protection. Dia : 100MM , Height ; 165MM And its should be Extruded Al.Housing with low glare MPO diffuser.The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions similiar to Arraystorm Lighting Model No: ASDL100SFXXIN015-165H | 15 | Nos | 1749 | 119.78 | 26235 | 1796.7 | 52 | 90948
n | Supply, Installation, Testing & Commissioning of LED Surface/Suspended Cylindrical Downlighter with a nominal system luminous efficacy >90Lm/W and Luminaire wattage ≈ 15W. Also Safe operating voltage 140-270V AC. Power factor should be >0.95 & THD should be <10% & CRI>80. SPD Should be 2.5KV Surge Protection. Dia : 100MM , Height ; 165MM And its should be Extruded Al.Housing with low glare MPO diffuser.The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions similiar to Arraystorm Lighting Model No: ASDL100SFXXIN015-165H - (with Dali Dimmable) | 5 | Nos | 4399 | 119.78 | 21995 | 598.9 | 0 | 0
o | Supply,Installation, Testing and Commisioining of single 4 feet ceiling/surface mount 18/20W LED batten type fittings with electronic driver and all accessories as per the site conditions (Including the earthing of fixture) similar to Arraystorm Lighting Model No: ASTB9002FFXXIN020 | 5 | Nos | 593.6 | 119.78 | 2968 | 598.9 | 5 | 2968
p | Decorative Lights |  |  | 0 | 0 | 740516 |  |  | 0 | 700532.8
|  |  |  | 0 | 0 |  |  |  | 0
1 | Supply, Installation, Testing and Commisioining of 450mm dia 60w decorative type fittings. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions approved by archeitech/consultant.Approx. Value of the fittings.Rs-5,000 | 12 | Nos | 5300 | 371 | 63600 | 4452 | 3 | 15900
2 | Supply, Installation, Testing and Commisioining of 450mm dia 60w decorative type fittings. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions approved by archeitech/consultant.Approx. Value of the fittings.Rs-10,000 | 6 | Nos | 10600 | 371 | 63600 | 2226 | 0 | 0
3 | Supply, Installation, Testing & Commissioning of LED Suspended Continous LED Linear Profile Light. Minimum Guaranteed Technical Parameters should be: UGR <19 , System Luminous efficacy >90Lm/W, CRI >80, THD <10, SDCM<5, IP20. Wattage: ≈20W/meter, LED CCT options: 5700/4000/3000 K. SPD should be provided with 3.5kV, Luminaire Dimension: L = 1000 mm X Width = 75 mm And its should be EXTRUDED AL Housing with Special grade low glare MPO diffuser. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions, | 10 | Mtr | 6360 | 265 | 63600 | 2650 | 6 | 38160
4 | Supply, Installation, Testing and Commisioining of 4500 X 300mm Panel type fittings. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions approved by archeitech/consultant.Approx. Value of the fittings is Rs 20,000 | 1 | Nos | 21200 | 795 | 21200 | 795 | 0 | 0
5 | Supply, Installation, Testing and Commisioining of Linear type decarartive LED fittings. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions approved by archeitech/consultant.Approx. Value of the fittings Minimum Guaranteed Technical Parameters should be: UGR <19 , System Luminous efficacy >90Lm/W, CRI >80, THD <10, SDCM<5, IP20. Wattage: ≈20W/meter, LED CCT options: 5700/4000/3000 K. SPD should be provided with 3.5kV, Luminaire Dimension: L = 5500 mm X Width = 75 mm | 2 | Nos | 116600 | 1590 | 233200 | 3180 | 2 | 233200
6 | Supply, Installation, Testing and Commisioining of 12w twin light fittings. The supply of accessories like clamps, supporting brackets and hardwares as required and interconnecting with 3 core 1.5 sqmm PVC insulated FRLS copper wire with all accessories required as per site conditions approved by archeitech/consultant. | 15 | Nos | 3180 | 265 | 47700 | 3975 | 0 | 0
|  |  |  | 0 | 0 | 492900 |  |  |  | 287260
| Sub Total | 506 |  | 0 | 0 | 2466832 | 103895.9
|  |  |  | 0 | 0
2 | WIRING FOR LUMINAIRES |  |  | 0 | 0
| MS Conduits only for the closed ceiling only, open office area wiring through powder coated closed tray |  |  | 0 | 0
I | MAIN LIGHT WIRING (PP) |  |  | 0 | 0
a | Supply, Laying, Testing and Commissioning of 3R 1.5Sq.mm PVC insulated FRLS copper wire with 20mm dia MS conduit along with Modular 6A one way switch with moulded front plate GI anodized enclosure and other associated accessories as required as per the site conditions. | 150 | Nos | 1280.48 | 479.12 | 192072 | 71868
b | Supply, Laying, Testing and Commisiosning of 3C 1.5sqmm PVC insulated unarmoured sheathed FRLS flexible multistrand copper cable(BLACK) in existing trays/raceways with Modular 6A one way switch with moulded front plate GI anodised enclosure and other associated accessories as required as per the site conditions. | 10 | Nos | 1296.38 | 479.12 | 12963.8 | 4791.2
|  |  |  | 0 | 0
II | SECONDARY LIGHT WIRING (SP) |  |  | 0 | 0
a | Supply, Laying, Testing and Commissioning of 3R 1.5Sqmm PVC insulated FRLS copper wire with 20mm dia MS conduit along with other associated accessories as required as per the site conditions. | 328 | Nos | 503.5 | 185.5 | 165148 | 60844
b | Supply, Laying, Testing and Commissioning of 2R 2.5Sqmm + 1R 1.5Sq.mm PVC insulated FRLS multistrand copper wire with 20mm dia MS conduit with all accessories as required as per site conditions.(lighting circuit mains) | 1500 | Mtrs | 193.98 | 66.78 | 290970 | 100170
c | Supply, Laying, Testing and Commissioning of 2R 2.5Sqmm + 1R 1.5S.mm PVC insulated FRLS multistrand copper wire in existing MS conduit with all accessories as required as per site conditions. | 350 | Mtrs | 89.04 | 25.44 | 31164 | 8904
d | Supply, Laying, Testing and Commissioning of 2R 1.5Sqmm + 1R 1.5Sq.mm PVC insulated FRLS Grey color multistrand copper wire with 25mm dia MS conduit with all accessories as required as per site conditions.(EL lighting circuit ) | 300 | Mtrs | 228.96 | 78.44 | 68688 | 23532
e | Supply, Laying, Testing and Commissioning of 2C 1.5sqmm PVC insulated unarmored sheathed FRLS flexible multistrand copper cable with MS conduit with all suitable accessories as reqd. | 50 | Mtrs | 151.58 | 58.3 | 7579 | 2915
| Sub Total |  |  | 0 | 0 | 768584.8 | 273024.2
3 | POWER OUTLETS (SOCKETS) The UPS Modular are with white colour front plate & Black/Grey colour for rawpower |  |  | 0 | 0
a | Supply, Fixing, Testing and Commisiosning of 3 nos 16A socket and 1 no 16A switch with moulded front plate GI anodised enclosure and other associated accessories in the work station as required as per the site conditions.(for UPS POWER) | 186 | Nos | 654.02 | 159 | 121647.72 | 29574
b | Supply, Fixing, Testing and Commisiosning of 2 nos 16A socket and 1 no 16A switch with moulded front plate GI anodised enclosure and other associated accessories in the work station as required as per the site conditions. | 46 | Nos | 491.84 | 137.8 | 22624.64 | 6338.8
c | Supply, Fixing, Testing and Commisiosning of 1 nos 6A 3/5 pin shurtred Type socket and 1 no 6A switch with moulded front plate GI anodised enclosure and other associated accessories in the work station as required as per the site conditions.(for RAW POWER) | 30 | Nos | 399.62 | 106 | 11988.6 | 3180
d | Supply, Fixing, Testing and Commisiosning of 1 no 16/6A switched socket with moulded front plate GI anodised enclosure and other associated accessories as per the site conditions. | 35 | Nos | 399.62 | 106 | 13986.7 | 3710
e | Supply, Fixing, Testing and Commisiosning of 1 no 16/6A switched socket with moulded front plate GI anodised enclosure and other associated accessories including chasing embedding rough plastering as required as per the site conditions. (with indicator) | 60 | Nos | 411.28 | 106 | 24676.8 | 6360
f | Supply, Fixing, Testing and Commisiosning of 1 no 16/6A spalsh proof switched socket with moulded front plate GI anodised enclosure and other associated accessories as per the site conditions.(for RAW POWER) | 5 | Nos | 657.2 | 106 | 3286 | 530
g | Supply, Fixing, Testing and Commissioning of 1 no 6A switched socket with moulded front plate GI anodized enclosure and other associated accessories as per the site conditions.(for RAW POWER) | 10 | Nos | 295.74 | 106 | 2957.4 | 1060
h | Supply, Fixing, Testing and Commissioning of 32A, 3 pin industrial type interlocked switched socket outlet with 32A DP MCB- D Curve and accessories and surface mounting box of IP 44 degree of protection with plug top and other associated accessories as required as per the site conditions. To be fixed in Ceiling trays or in the floor near server/hub rack | 6 | Nos | 3392 | 371 | 20352 | 2226
i | Supply, Fixing, Testing and Commissioning of 32A, 5 pin industrial type interlocked switched socket outlet with 32A TP+2N RCBO with supporting accessories and surface mounting box of IP 44 degree of protection with plug top and other associated accessories as required as per the site conditions. | 1 | Nos | 9010 | 371 | 9010 | 371 |  |  |  | 2166.6667
j | Supply, Fixing, Testing and Commissioning of 32A, 3pin industrial type metal socket outlet controlled by a 32A DP RCBO enclosed in MS Enclosure with plug top and other associated accessories as required as per the site conditions. | 4 | Nos | 4770 | 371 | 19080 | 1484
k | Supply, Fixing, Testing and Commissioning of 63A 4P 100mA RCBO enclosed in weather proof Enclosure with and other associated accessories as required as per the site conditions. | 1 | Nos | 5384.8 | 371 | 5384.8 | 371
l | Supply, Fixing, Testing and Commissioning of 40A 4P 100mA RCBO enclosed in weather proof Enclosure with and other associated accessories as required as per the site conditions. | 5 | Nos | 5384.8 | 371 | 26924 | 1855
m | Supply, Fixing, Testing and Commissioning of 63A TPN MCB enclosed in weather proof Enclosure with and other associated accessories as required as per the site conditions. | 1 | Nos | 3116.4 | 371 | 3116.4 | 371
n | Supply, Fixing, Testing and Commissioning of 40A TPN MCB enclosed in weather proof Enclosure with and other associated accessories as required as per the site conditions. | 1 | Nos | 3116.4 | 371 | 3116.4 | 371
o | Supply, Fixing, Testing and Commissioning of 20/32A DP MCB enclosed in Enclosure with and other associated accessories as required as per the site conditions. | 1 | Nos | 2556.72 | 371 | 2556.72 | 371
p | Supply and Fixing of 3Module Data/Voice PVC Enclosure box with other associated accessories as required as per the site conditions. | 40 | Nos | 68.9 | 15.9 | 2756 | 636
q | Supply and Fixing of 250A 4PMCCB with MFM along with suitable CTs Breaker In the Exisitng Panel with other all associated accessories as required as per the site conditions. | 1 | Nos | 82000 | 9010 | 82000 | 9010
|  |  |  | 0 | 0
| Sub Total |  |  | 0 | 0 | 375464.18 | 67818.8
|  |  |  | 0 | 0
4 | CABLING FOR POWER OUTLETS |  |  | 0 | 0
| UPS/RAW POWER WIRING |  |  | 0 | 0
a | Supply, Laying, Testing and Commissioning of 3C 2.5sqmm PVC insulated unarmored sheathed FRLS flexible multistrand copper cable(WHITE) in trays / raceways with all accessories as reqd.(6/16A Ups socket) | 3400 | Mtrs | 94 | 15.9 | 319600 | 54060
b | Supply, Laying, Testing and Commissioning of 3C 2.5sqmm PVC insulated unarmored sheathed FRLS flexible multistrand copper cable (WHITE) with suitable MS conduits with all accessories as reqd.(16A Ups socket) | 1000 | Mtrs | 190 | 53 | 190000 | 53000
c | Supply, Laying, Testing and Commissioning of 3C 2.5sqmm PVC insulated unarmored sheathed FRLS flexible multistrand copper cable(BLACK) in trays/raceways with all suitable accessories as reqd. (Raw power socket) | 1500 | Mtrs | 94 | 15.9 | 141000 | 23850
d | Supply, Laying, Testing and Commissioning of 3C 2.5sqmm PVC insulated unarmored sheathed FRLS flexible multistrand copper cable(BLACK) with MS conduit with all suitable accessories as reqd.( 6A Raw power socket) | 500 | Mtrs | 190 | 53 | 95000 | 26500
e | Supply, Laying, Testing and Commissioning of 3C 4sqmm PVC insulated unarmored sheathed FRLS flexible multistrand copper cable with MS conduit with all suitable accessories as reqd. | 250 | Mtrs | 254.4 | 59.36 | 63600 | 14840
f | Supply, Laying, Testing and Commissioning of 3C4sqmm PVC insulated unarmored sheathed FRLS flexible multistrand copper cable in trays / raceways with all accessories as reqd. | 50 | Mtrs | 148.4 | 23.32 | 7420 | 1166
g | Supply, Laying, Testing and Commissioning of 3C 1.5sqmm PVC insulated unarmored sheathed FRLS flexible multistrand copper cable with FR PVC conduit with all suitable accessories as reqd. | 20 | Mtrs | 67.045 | 21.2 | 1340.9 | 424
|  |  |  | 0 | 0
| Sub Total |  |  | 0 | 0 | 817960.9 | 173840
5 | UNDER FLOOR CABLE MANAGEMENT SYSTEM |  |  | 0 | 0 | 0 | 0
I | Supply, Fixing of Aluminium Trunking box of 1.6mm thick and should be earthed every 3meters with 2.5sqmm copper wire, 60MM floor cutting, removing the debris, plastering with propoer checkan mesh Clamps and all other accessories as required as per the site condition for fixing the same. (the proper couplers to be used in between the joining of raceways) |  |  | 0 | 0 | 0 | 0
a | 50 x 25 mm Aluminium Channel | 10 | Mtrs | 530 | 318 | 5300 | 3180
b | 100 x 45mm Aluminium Channel | 350 | Mtrs | 636 | 318 | 222600 | 111300
|  |  |  | 0 | 0
| Sub Total |  |  | 0 | 0 | 227900 | 114480
6 | UNDER FLOOR JUNCTION BOXES |  |  | 0 | 0 | 0 | 0
II | Supply, Fixing, Erection of Powder coated MS Junction box of following sizes.The MS junction box shall be earthed with 2.5sqmm copper wire with all hard wares and accessories as required including all clamps and hard wares for fixing the same. The proper supporting to be provided in the centre of the Junction Boxes. The Junction to be covered all other sides, excluding the entry side. The junction thickness is 2mm and top cover 3mm. |  |  | 0 | 0 | 0 | 0
a | 150 x 150 x 50mm | 115 | Nos | 275.6 | 159 | 31694 | 18285
b | 250 x 250 x 50mm | 13 | Nos | 318 | 159 | 4134 | 2067
c | 350 x 350 x 50mm | 6 | Nos | 477 | 159 | 2862 | 954
d | 450 x 450 x 50mm | 6 | Nos | 948.7 | 328.6 | 5692.2 | 1971.6
|  |  |  | 0 | 0
f | Supply, Fixing, Erection of following size EGA Junction box with all hard wares and accessories as required including all clamps and hard wares for fixing the same. the unused side of the junction box to be covered with 14SWG sheet. |  |  | 0 | 0
| 350 x 350 x 50mm | 1 | Nos | 9010 | 530 | 9010 | 530
| Sub Total |  |  | 0 | 0 | 53392.2 | 23807.6
7 | SECONDARY DISTRIBUTION SYSTEMS |  |  | 0 | 0
a | Supply, Installation, Testing and Commissioning of three phase, phase segregated, compartmentalized 8 way MCBDB Double door type, IP 42 powder coated comprising of "C" curve MCB's for LIGHTING DB. |  |  | 0 | 0
| Incommer - 40A TPN MCB - 1 No |  |  | 0 | 0
| Phase Incommer - 40A 30mA DP RCBO- 3Nos |  |  | 0 | 0
| Outgoings - 6A SP MCB - 24 Nos |  |  | 0 | 0
| Blank Plates - 0 |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
b | Supply, Installation, Testing and Commissioning of three phase, phase segregated, compartmentalized 12way MCBDB Double door type, IP 42 powder coated comprising of "C" curve MCB's for LIGHTING DB. |  |  | 0 | 0
| Incommer - 40A TPN MCB - 1 No |  |  | 0 | 0
| Phase Incommer - 40A 30mA DP RCBO- 3Nos |  |  | 0 | 0
| Outgoings - 6A SP MCB - 36 Nos |  |  | 0 | 0
| Blank Plates - 0 |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 2 | Nos | 26430.04 | 3074 | 52860.08 | 6148
|  |  |  | 0 | 0
c | Supply, Installation, Testing and Commissioning of three phase, phase segregated, compartmentalized 8 way MCBDB Double door type, IP 42 powder coated comprising of "C" curve MCB's for POWER DB. |  |  | 0 | 0
| Incommer - 63A TPN MCB - 1 No |  |  | 0 | 0
| Phase Incommer -63A 30mA DP RCBO - 3Nos |  |  | 0 | 0
| Outgoings - 16A SP MCB - 24Nos |  |  | 0 | 0
| Blank Plates - 0 |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 2 | Nos | 25056.28 | 2353.2 | 50112.56 | 4706.4
|  |  |  | 0 | 0
d | Supply, Installation, Testing and Commissioning of three phase, phase segregated, compartmentalized 12 way MCBDB Double door type, IP 42 powder coated comprising of "C" curve MCB's for POWER DB. |  |  | 0 | 0
| Incommer - 63A TPN MCB - 1 No |  |  | 0 | 0
| Phase Incommer -63A 30mA DP RCBO - 3Nos |  |  | 0 | 0
| Outgoings - 16A SP MCB - 36 Nos |  |  | 0 | 0
| Blank Plates - 0 |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
e | Supply, Installation, Testing and Commissioning of three phase, phase segregated, compartmentalized 12way MCBDB Double door type, IP 42 powder coated comprising of "D" curve MCB's for UPS DB. |  |  | 0 | 0
| Incommer - 63A TP+2N MCB - 1 No |  |  | 0 | 0
| Phase Incommer - 63A DP SI TYPE 30mA RCBO - 3Nos |  |  | 0 | 0
| Outgoings - 16A SP MCB - 36 Nos |  |  | 0 | 0
| Blank Plates - 0 |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 2 | Nos | 40110.4 | 3074 | 80220.8 | 6148
|  |  |  | 0 | 0
f | Supply, Installation, Testing and Commissioning of three phase, phase segregated, compartmentalized 8way MCBDB Double door type, IP 42 powder coated comprising of "D" curve MCB's for UPS DB.( LV DB) |  |  | 0 | 0
| Incommer - 63A TP+2N MCB - 1 No |  |  | 0 | 0
| Phase Incommer - 63A DP SI TYPE 30mA RCBO - 3Nos |  |  | 0 | 0
| Outgoings - 16A SP MCB - 24 Nos |  |  | 0 | 0
| Blank Plates - 0 |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 0 | Nos | 44435.2 | 3535.1 | 0 | 0
|  |  |  | 0 | 0
g | Supply, Installation, Testing and Commissioning of single phase, 16 way MCBDB Double door type, IP 42 powder coated comprising of "C" curve MCB's for EMERGENCY LDB. |  |  | 0 | 0
| Incommer -25A DP 30mA RCBO - 1 No |  |  | 0 | 0
| Outgoings - 6A SP MCB - 14 Nos |  |  | 0 | 0
| Blank Plates - 0 |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 1 | Nos | 6755.38 | 1293.2 | 6755.38 | 1293.2
|  |  |  | 0 | 0
h | Supply, Installation, Testing and Commissioning of single phase, 16 way MCBDB Double door type, IP 42 powder coated comprising of "C" curve MCB's for M LDB. |  |  | 0 | 0
| Incommer -32A DP MCB - 1 No |  |  | 0 | 0
| Outgoings - 25A DP MCB - 4 Nos |  |  | 0 | 0
| Blank Plates - 0 |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
I | Supply, Installation, Testing and Commissioning of Three phase, 4way TPN MCBDB Double door type, IP 42 powder coated comprising of "D" curve MCB's for HUB UDB. |  |  | 0 | 0
| Incommer -63A TP+2N MCB - 1 No |  |  | 0 | 0
| Phase Incommer -63A 30mA DP RCBO si type - 3Nos |  |  | 0 | 0
| Outgoings -25/32A SP MCB - 12Nos |  |  | 0 | 0
| Blank Plates - 0 |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 2 | Nos | 32127.54 | 1632.4 | 64255.08 | 3264.8
|  |  |  | 0 | 0
j | Supply, Installation, Testing and Commissioning of three phase, phase segregated, compartmentalized 8 way MCBDB Double door type, IP 42 powder coated comprising of "C" curve MCB's for AC DB. |  |  | 0 | 0
| Incommer - 63A TPN MCB - 1 No |  |  | 0 | 0
| Phase Incommer -63A 30mA DP RCBO - 3Nos |  |  | 0 | 0
| Outgoings - 16A SP MCB - 24Nos |  |  | 0 | 0
| Blank Plates - 0 |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
k | Supply, Installation, Testing and Commissioning of three phase, IP 42 powder coated comprising of FABRICATED KITCHEN DB |  |  | 0 | 0
| Incommer - 100A 4P MCCB - 1 No |  |  | 0 | 0
| Outgoings - 40A TPN RCBO 30mA RCBO -4 Nos |  |  | 0 | 0
| Outgoings - 32A DP RCBO 30mA RCBO -8Nos |  |  | 0 | 0
| Including all interconnections and other associated fixing accessories etc as reqd as per the site conditions. | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
| Sub Total |  |  | 0 | 0 | 254203.9 | 21560.4
8 | PRIMARY DISTRIBUTION SYSTEM (Note: All the breakers should be Ics = 100% Icu and with pad lock arrangement for handles) |  |  | 0 | 0 | 0 | 0
| CTs shall be with dual ratio and cast resin type only All doors to have rubber gasket with shutter assembly & door seating frame. All MCCBs of 250A and above for non-ups loads will be microprocessor based only and for UPS panels shall be with thermal releases. |  |  | 0 | 0 | 0 | 0
| POWER PANEL & UPS O/G PANELS cable Entry Top & bottam. Other panels will be top |  |  | 0 | 0
| • The ATS system should be a 4 pole switch version AC23duty of required ratings with fail proof mechanical interlocking and certified to IEC60947-6-1&60947-3 having CE marking and with 3 distinct positions I -0-II.The ATS rating shall be confirming to AC31B category of IEC60947-6-1 when used close to incomers and shall be AC32B when used as incomers for mixed loads and AC33B when used directly for motor loads. The combination of Motorised Switch + ATS controller should be certified and supplied by the manufacturer as compliant to IEC 60947-6-1, • It should come with aseparate ATS controller wired to motorized Switch unit,with LED’s mimic display of 2 sources, to sense loss of power , single phasing,overvoltage,under voltage ,over frequency and under frequency and send commands for changeover to the stable source for this conditions..It should have required timers for the time delays for transfer from Source 1 to source 2 and vice versa.The controller shall be mounted on the door of the panel . • Motor mechanism when used in the ATS should be field replaceable at site without disturbing power cables and power supply.Motor mechanism should be capable of operating between 166V- 332 V AC for a normal control supply of 230V AC • The Motor Mechanism should have independent Watch dog relay to monitor healthiness of the same and indicate thro Alarm contact in case of a fault • It should have a manual on load changeover capability at full load with the emergency handle to be supplied. It should be possible to padlock in Zero position for safety purpose in order to have a safe maintenance facility on the load side. |  |  | 0 | 0
| a) The Cost to include Supply, Installation Testing & Commissioning of 3 kg Automatic Direct pressure Release LPCB (LPS 1666) approved System for Electrical Panel application utilising 2Kg or 3kg Novec 1230/ FK5-1-12/ FK5-1-12 clean agent for Electrical Panels panels. The tested system must be approved for Enclosed and Ventilated (Natural and Forced Airlflow) Electrical Panels. The cylinder made of mild steel TPED approved along with sturdy metal bracket having direct low pressure dual discharge valve having safety brust disc for over pressurization and ball valve with open and closed option. The DLP valve having push in connector for tube to be connected with double push mechanism. The pressure guage having integrated pressure switch for visual and automatic monitoring of system pressure . The clean agent Novec 1230/ FK5-1-12/ FK5-1-12 to be filled in approved filling plant. The heart of the system linear heat sensing tube made of special polymer red colour 4mm I.D. 6mm O.D. pressurized with Nitrogen to be installed as per the OEM Manual. All the tube fittings to be OEM supplied .The system to be designed,installed and commisioned as per system manual approved by LPCB. The system installer to be trained and certiifed by OEM of the system activation during gas discharge with Complete heat-sensitive tubing throughout panels as required, Fire Alarm & Control Unit (Direct System) b) The required Floor Stands & other accessories to mount the panel to be considered in Costing] |  |  | 0 | 0
a | POWER PANEL |  |  | 0 | 0
| Supply, Erection, Testing and Commissioning of Indoor type Floor Power panel floor mounting type, dust and vermin proof by construction of 14 SWG CRCA sheets Compartmentalised,all MCCB shall have inbuilt shunt trip coil arrangement and All MCCBs of 250A and above for non-ups loads will be microprocessor based , CTs shall be with dual ratio and cast resin type only.with modular type IP 42 Protection with powder coated panel as specification below |  |  | 0 | 0
| Incomer: |  |  | 0 | 0
| 1Nos -250A 4P ATS WITH CONTROLLER & 36kA 250A 4P MCCB BMS integriation for status monitering |  |  | 0 | 0
| 1 Set of Current transformer rated 250/5A, 10VA/CI 1.0 for metering. |  |  | 0 | 0
| 1 No – Digital Multi data Meter with RS 485 |  |  | 0 | 0
| 1 Set – LED type RYB indication lamps with control fuses,In coming breakers shall have LED 'ON / OFF / TRIP' |  |  | 0 | 0
| 1 Set - ELR with CBCT.(500mA S) |  |  | 0 | 0
| 1 No of TVSS 36kA connected to the Bus Bar. |  |  | 0 | 0
| Outgoing: |  |  | 0 | 0
| 2Nos - 125A TPN MCCB |  |  | 0 | 0
| 1Nos - 63A TPN MCCB |  |  | 0 | 0
| 10Nos - 40A TPN MCCB |  |  | 0 | 0
| 1No- 63A TPN MCCB Sub Outgoings: a) 25A DP MCB-3Nos. |  |  | 0 | 0
| 250A Aluminium Bus Bar and Associated Accessories as required. |  |  | 0 | 0
| Incoming and outgoing cables shall be of Top entry only. | 1 | Sets | 633880 | 37100 | 633880 | 37100
|  |  |  | 0 | 0
b | W/S UPS O/P PANEL |  |  | 0 | 0
| Supply, Erection, Testing and Commissioning of Indoor type UPS OUTGOING PANEL, Floor/Wall mounting type, dust and vermin proof by construction of 14 SWG CRCA sheets Compartmentalized, cable entry shall be in both top and bottom,All MCCBs of 250A and above for non-ups loads will be microprocessor based only and for UPS panels shall be with thermal releases. , CTs shall be with dual ratio and cast resin type only.with modular type IP 42 Protection with powder coated panel as specification below and it CT should connected in common main bus.All MCB should be 'D' curve. |  |  | 0 | 0
| Incomer: |  |  | 0 | 0
| 2Nos -100A TP+2N MCCB (Neutral should be 200% of the Phase Current) |  |  | 0 | 0
| 2Set of Current transformer rated 100/5A, 10VA/CI 1.0 for metering at common bus. |  |  | 0 | 0
| 2Nos – Digital Multi data Meter with RS 485 (suitable to measure harmonics) at common bus. |  |  | 0 | 0
| 2Sets – LED type RYB indication lamps with control fuses,In coming breakers shall have LED 'ON / OFF / TRIP' |  |  | 0 | 0
| Outgoing: |  |  | 0 | 0
| 6Nos - 63A TP+2N MCB |  |  | 0 | 0
| 200A TP+2N Copper Bus Bar and Associated Accessories as required. (Neutral should be 200% of the Phase Current) | 1 | Sets | 127200 | 26500 | 127200 | 26500
| Incoming and outgoing cables shall be of Top& Bottom entry. |  |  | 0 | 0
|  |  |  | 0 | 0
| Sub Total |  |  | 0 | 0 | 761080 | 63600
9 | POWER CABLES AND CABLE TERMINATION |  |  | 0 | 0
I | Supply, Laying, Testing and Commissioning of 1100V PVC insulated XLPE and sheathed Armoured/Unarmoured Copper / Aluminium Conductor cables laid over MS supports / Cable racks /fixing of walls including clamping the cable to the support in all approved manner as all complete required. End cable termination lugs shall be as per the respected cable size with respected gland and also double compression gland shall be provide for the 25Sqmm above cable size with double gland earthing to be considered and other accessories to be provided as required as per the site condition. |  |  | 0 | 0
|  |  |  | 0 | 0
| Aluminium Armoured cable XLPE |  |  | 0 | 0
a | 3.5C 240 sq.mm XLPE AR AL Cable | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
b | 3.5C 185 sq.mm XLPE AR AL Cable | 250 | Mtrs | 1005.94 | 162.18 | 251485 | 40545
| And it terminations | 4 | Nos | 1221.12 | 539.54 | 4884.48 | 2158.16
|  |  |  | 0 | 0
c | 3.5C 120 sq.mm XLPE AR AL Cable | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
d | 3.5C70 sq.mm XLPE AR AL Cable | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
e | 3.5C 50 sq.mm XLPE AR AL Cable | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
f | 3.5C 25 sq.mm XLPE AR AL Cable | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
g | 4C 16 sq.mm AR Aluminium Cable | 320 | Mtrs | 159 | 53 | 50880 | 16960
| And it terminations | 20 | Nos | 424 | 159 | 8480 | 3180
|  |  |  | 0 | 0
h | 4C 10 sq.mm AR Aluminium Cable | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
| Copper Armoured cable (UPS AND INVERTER DB'S) |  |  | 0 | 0
i | 4C 70 sq.mm Ar. Copper Cable YFY | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
j | 4C25 sq.mm Ar. Copper Cable YFY | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
k | 4C 16 sq.mm Ar. Copper Cable YFY | 120 | Mtrs | 964.6 | 61.48 | 115752 | 7377.6
| And it terminations | 8 | Nos | 854.36 | 286.2 | 6834.88 | 2289.6
|  |  |  | 0 | 0
l | 4C10 sq.mm Ar. Copper Cable YFY | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
m | 4C6 sq.mm Ar. Copper Cable YFY | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
n | 3C6 sq.mm Ar. Copper Cable YFY | 30 | Mtrs | 329.978 | 33.92 | 9899.34 | 1017.6
| And it terminations | 2 | Nos | 201.4 | 95.4 | 402.8 | 190.8
|  |  |  | 0 | 0
o | 3C4 sq.mm Ar. Copper Cable YFY | 40 | Mtrs | 228.536 | 29.68 | 9141.44 | 1187.2
| And it terminations | 4 | Nos | 180.2 | 95.4 | 720.8 | 381.6
|  |  |  | 0 | 0
p | 3C2.5 sq.mm Ar. Copper Cable YFY | 20 | Mtrs | 198.22 | 26.5 | 3964.4 | 530
| And it terminations | 2 | Nos | 159 | 84.8 | 318 | 169.6
|  |  |  | 0 | 0
| Copper Unarmoured cable (UPS SYSTEM and EARTHING) |  |  | 0 | 0
q | 1C 185 sq.mm Copper Cable YY | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
r | 1C 150 sq.mm Copper Cable YY | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
s | 1C 120 sq.mm Copper Cable YY | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
t | 1C 95 sq.mm Copper Cable YY | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
u | 1C 70 sq.mm Copper Cable YY | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
v | 1C 50 sq.mm Copper Cable YY | 0 | Mtrs | 0 | 0 | 0 | 0
| And it terminations | 0 | Nos | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
w | 1C 35 sq.mm Copper Cable YY | 400 | Mtrs | 606.32 | 57.24 | 242528 | 22896
| And it terminations | 40 | Nos | 222.6 | 106 | 8904 | 4240
|  |  |  | 0 | 0
x | 1C 25 sq.mm Copper Cable YY | 400 | Mtrs | 166.42 | 296.8 | 66568 | 118720
| And it terminations | 6 | Nos | 21.2 | 162.18 | 127.2 | 973.08
|  |  |  | 0 | 0
y | 1C 16 sq.mm Copper Cable YY | 300 | Mtrs | 166.42 | 296.8 | 49926 | 89040
| And it terminations | 6 | Nos | 21.2 | 162.18 | 127.2 | 973.08
|  |  |  | 0 | 0
z | 1C 10 sq.mm Copper Cable YY | 180 | Mtrs | 136.422 | 29.68 | 24555.96 | 5342.4
| And it terminations | 18 | Nos | 59.36 | 41.34 | 1068.48 | 744.12
|  |  |  | 0 | 0
aa | 1C 6 sq.mm Copper Cable YY | 240 | Mtrs | 69.96 | 23.32 | 16790.4 | 5596.8
| And it terminations | 12 | Nos | 47.7 | 21.2 | 572.4 | 254.4
|  |  |  | 0 | 0
ab | 1C 4 sq.mm Copper Cable YY | 60 | Mtrs | 52.47 | 15.9 | 3148.2 | 954
| And it terminations | 4 | Nos | 37.1 | 21.2 | 148.4 | 84.8
|  |  |  | 0 | 0
| Sub Total |  |  | 0 | 0 | 877227.38 | 325805.84
|  |  |  | 0 | 0
10 | CEILING CABLE MANAGEMENT SYSTEM |  |  | 0 | 0
a | Supply and fixing of Profile design Perforated Cable tray with horizontal & vertical bends, reducers, Tee's, cross over , suitable supports and brackets and other accessories as required confirming to IS / IEC-61537. The Tray shall be galvanized for corrosion protection as per ISO 1461. .The trays should be tested for a safe working load as per the standard with a span distance of 1.5 meters and the deflection should be within the limits as per NEMA standards. The tray covers shall be snap fitted. The perforated tray shall be supplied with the standard length of 3 Mtr . The Bottom tray thickness shall be 1.6 mm & Cover thickness shall be 1.6mm. .The trays shall include necessary couplers. |  |  | 0 | 0
i | 600 mm width x 75mm Height with cover | 10 | Mtrs | 2317.266 | 286.2 | 23172.66 | 2862
ii | 500 mm width x 75mm Height with cover | 0 | Mtrs | 0 | 0 | 0 | 0
iii | 450 mm width x 75mm Height with cover | 25 | Mtrs | 1616.076 | 254.4 | 40401.9 | 6360
iv | 400 mm width x 75mm Height with cover | 0 | Mtrs | 0 | 0 | 0 | 0
v | 300 mm width x 75mm Height with cover | 25 | Mtrs | 1144.164 | 212 | 28604.1 | 5300
vi | 200 mm width x 75mm Height with cover | 20 | Mtrs | 862.575 | 180.2 | 17251.5 | 3604
vii | 150 mm width x 75mm Height with cover | 10 | Mtrs | 718.998 | 137.8 | 7189.98 | 1378
vii | 100 mm width x 75mm Height with cover | 0 | Mtrs | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
b | Supply and fixing of Profile design Non Perforated Powder coated Cable tray / Ceiling Raceways with horizontal & vertical bends, reducers, Tee's, cross over , suitable supports and brackets and other accessories as required confirming to IS / IEC-61537. The Tray shall be galvanized for corrosion protection as per IS 277. .The trays should be tested for a safe working load as per the standard with a span distance of 1.5 meters and the deflection should be within the limits as per NEMA standards. The tray covers shall be snap fitted. The trays shall be supplied with the standard length of 3 Mtr . The Bottom tray thickness shall be 1.2 mm upto 200 mm W Trays & 1.5 mm from 300 mm and above widths & Cover thickness shall be 1.2mm. .The trays shall include necessary couplers and proper angle supports from ceiling |  |  | 0 | 0 | 0 | 0
i | 600 mm width x 75mm Height with cover | 0 | Mtrs | 0 | 0 | 0 | 0
ii | 500 mm width x 75mm Height with cover | 0 | Mtrs | 0 | 0 | 0 | 0
iii | 450 mm width x 75mm Height with cover | 30 | Mtrs | 1531.912 | 201.4 | 45957.36 | 6042
iv | 400 mm width x 75mm Height with cover | 0 | Mtrs | 0 | 0 | 0 | 0
v | 300 mm width x 75mm Height with cover | 60 | Mtrs | 1222.18 | 169.6 | 73330.8 | 10176
vi | 200 mm width x 75mm Height with cover | 0 | Mtrs | 0 | 0 | 0 | 0
vii | 150 mm width x 75mm Height with cover | 50 | Mtrs | 710.2 | 137.8 | 35510 | 6890
vii | 100 mm width x 75mm Height with cover | 0 | Mtrs | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
c | Supply and fixing of Cable Ladder with horizontal & vertical bends, reducers, Tee's,Cross over, supports, brackets and other accessories as required confirming to IS/IEC-61537.The Cable Ladder shall be made of 1.5mm thick sheet steel upto 600mm & 2.0mm thick upto 1000mm.The cable Ladder shall be 275 GSM strip galvanized sheet steel for corrosion protection confirming to DIN EN 10346 .The cable ladder should be tested for safe working load of 225 Kg/ Mtr with a span distance of 2 Mtr the deflection should be within the limits as per standard. The cable ladder shall be supplied in standard length of 3000 mm. The rung size shall be of 30x15mmm size suitable for fixing the cable clamps the space between the rungs shall be 300mm. |  |  | 0 | 0 | 0 | 0
i | 1000 mm Width 75 mm Height | 0 | Mtrs | 0 | 0 | 0 | 0
ii | 750 mm Width 75 mm Height | 0 | Mtrs | 0 | 0 | 0 | 0
iii | 600 mm Width 75 mm Height | 10 | Mtrs | 636 | 254.4 | 6360 | 2544
iv | 450 mm Width 75 mm Height | 0 | Mtrs | 0 | 0 | 0 | 0
v | 300 mm Width 75 mm Height | 5 | Mtrs | 477 | 174.9 | 2385 | 874.5
vi | 200 mm Width 75 mm Height | 0 | Mtrs | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
d | Supply and fixing of Perforated Cable tray with horizontal & vertical bends, reducers, Tee's, cross over , suitable supports and brackets and other accessories as required confirming to IS/IEC-61537. The Tray should be 275 GSM Strip galvanized sheet steel for corrosion protection confirming to DIN EN 10346. The trays should be tested for a safe working load of 185 Kgs with a span distance of 1.5 meters and the deflection should be within the limits as per standard. The safety factor shall be 1.7 times of the safe working load. The perforated tray shall be supplied with the standard length of 3 Mtr |  |  | 0 | 0 | 0 | 0
i | 500 mm width x 100mm Height x 3000 mm Length | 0 | Mtrs | 0 | 0 | 0 | 0
ii | 400 mm width x 100mm Height x 3000 mm Length | 0 | Mtrs | 0 | 0 | 0 | 0
iii | 300 mm width x 100mm Height x 3000 mm Length | 0 | Mtrs | 0 | 0 | 0 | 0
iv | 200 mm width x 100mm Height x 3000 mm Length | 10 | Mtrs | 1100.28 | 174.9 | 11002.8 | 1749
v | 150 mm width x 100mm Height x 3000 mm Length | 0 | Mtrs | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
e | Providing and Fixing of Cableoffill wire mesh cable tray system made outof stainless stell wires [316L AS PER NF 10-088-2] and bent into final shape , All cable trays, shall be manufactured with a longitudinal ‘T-welded’ safety edge and Trays shall be constructed with a 50 mm x 100 mm mesh configuration complete with couplers,C mountings and all accessories as required. |  |  | 0 | 0
i | 600 x 200mm Size | 0 | Mtrs | 0 | 0 | 0 | 0
ii | 450 x 100mm Size | 0 | Mtrs | 0 | 0 | 0 | 0
|  |  |  | 0 | 0
| Sub Total |  |  | 0 | 0 | 291166.1 | 47779.5
11 | EARTHING |  |  | 0 | 0
| Designing, S I T & C of earth station as per IS 3043, with proper earth lead connection arrangements. Rate shall include all materials excavation, refilling, compacting providing 2' dia/ 450 x 450mm 9" thick brick masonry, GI funnel, salt and char coal, hinged cover thick brick masonry, GI funnel, salt and char coal, hinged cover fabricated out of angle iron frame and 7mm thick chequered plate etc., complete. The GI funnel and tapping connection shall not be greater than 10" from the finished floor level. |  |  | 0 | 0
|  |  |  | 0 | 0
a | With 600 x 600 x 3mm Copper plate electrode |  | Nos | 0 | 0
b | With 100mm dia 3M long CI Pipe electrode |  | Nos | 0 | 0
c | Chemical Earthing Copper Coated: T-39 Cu. (80mm dia) - 3 mtrs with Back Fill Compund (25 kgs per Bag) includes Providing of RCC Chamber and Civil finishing including painting. | 2 | Nos | 19080 | 3710 | 38160 | 7420
d | Chemical Earthing Copper Coated: T-39 Cu. (40mm dia) - 3 mtrs with Back Fill Compund (25 kgs per Bag) includes Providing of RCC Chamber and Civil finishing including painting. | 2 | Nos | 15900 | 3710 | 31800 | 7420
| Sub Total |  |  | 0 | 0 | 69960 | 14840
12 | EARTH FLAT BUS |  |  | 0 | 0
a | Supply & Laying of 25x3mm GI. Flat | 300 | Mtrs | 79.5 | 21.2 | 23850 | 6360
b | Supply & Laying of 25x6mm GI. Flat | 200 | Mtrs | 174.9 | 31.8 | 34980 | 6360
b | Supply & Laying of 50x6mm GI. Flat | 0 | Mtrs | 0 | 0 | 0 | 0
c | Supply & Laying of 25x3mm cu. Flat | 0 | Mtrs | 0 | 0 | 0 | 0
d | Supply & Laying of 25x1.3mm cu. Flat | 0 | Mtrs | 0 | 0 | 0 | 0
d | Supply & Laying of 10 SWG bare Cu. Wire | 250 | Mtrs | 127.2 | 7.42 | 31800 | 1855
e | Supply and Installation of 12 way 25x6mm copper earth bus in powder coated box with vision sheet and all accessories as required. | 1 | Nos | 2047.92 | 299.98 | 2047.92 | 299.98
f | Supply and Installation of 12 way 25x3mm copper earth bus in powder coated box with vision sheet and all accessories as required. | 1 | Nos | 1335.6 | 159 | 1335.6 | 159
|  |  |  | 0 | 0
| Sub Total |  |  | 0 | 0 | 94013.52 | 15033.98
13 | SAFETY EQUIPMENTS |  |  | 0 | 0 | 0 | 0
a | 1100V Rubber mat as per latest IS 15652/2006 non skid rubber mat 2mm thick and 900 mm width. | 1 | Nos | 1325 | 106 | 1325 | 106
b | First Aid Box | 1 | Nos | 2650 | 106 | 2650 | 106
c | First Aid Chart (English & Local language) | 1 | Nos | 756.84 | 106 | 756.84 | 106
| Sub Total |  |  | 0 | 0 | 4731.84 | 318
14 | ASSOCIATED ACCESSORIES |  |  | 0 | 0 | 0 | 0
1 | Supply and fixing of 2mm thick PVC/MS conduit of various dia., exposed or concealed, with all accessories and fish wire. |  |  | 0 | 0 | 0 | 0
a | Supply and Fixing of 1" PVC Conduits | 150 | Mtrs | 47.7 | 23.32 | 7155 | 3498
b | Supply and Fixing of 1 1/4" PVC Conduits | 250 | Mtrs | 83.74 | 28.62 | 20935 | 7155
c | Supply and Fixing of 2" PVC Conduits | 50 | Mtrs | 137.8 | 21.2 | 6890 | 1060
d | Supply and Fixing of 1" MS Conduits | 0 | Mtrs | 0 | 0 | 0 | 0
e | Supply and Fixing of 2" MS Conduits | 0 | Mtrs | 0 | 0 | 0 | 0
f | Supply and Fixing of 1" GI hose | 0 | Mtrs | 0 | 0 | 0 | 0
g | Power coated pole with junction box for Sensor mounting as per site condutions | 20 | Nos | 636 | 53 | 12720 | 1060
h | Supply and Installation of M.S. Material for SB, DB's supports, iron embeded in the wall, steel structure in open Area painted with two coats of primer and two coats of enamel paint. | 300 | Kgs | 100.7 | 21.2 | 30210 | 6360
2 | TEMPORARY LIGHTING AND POWER | 0 |  | 0 | 0 | 0 | 0
i | Temporary Lighting & Power arrangement with sufficient temporary Lighting ( Min 200Lux Ave. ) & power shall be provided to all agencies during execution with the following requirements ( Electrician to be required for 2 shifts) | 1 | L.S | 100.7 | 21.2 | 100.7 | 21.2
ii | Considering 24/7 lighting for all the equal distance (minimum 15 feet ) 4feet (36w)Patti light fittings, all the passage with the 4feet tube fittings on equal distance and all the enclosed area to be provided with light fixtures until the project works are completed. |  |  | 0 | 0
iii | The main power shall be tapped from builder source will have the respected range of energy meter with, each and every Distribution board/Panel incoming cable shall have proper type of gland and its earthing, also body earthing and RCCB to be provided. |  |  | 0 | 0
iv | All office area to be provided with sufficiant distribution board in equal distance, each should be equipped with the required industrial plug top socket with all the safety protection features. ( minimum 2nos of 3phase socket & 5Nos single sockets required) |  |  | 0 | 0
v | All the entry/temporary toilets/ path ways ,staircases, vendor store area, material stacking place to be provided with adequate lighting with 4feet Patti fitting on the equal distance (minimum 4.5meter). |  |  | 0 | 0
vi | Patty fitings will cover to be provided. Cost to include associated cabling and replacements. Emergency lights to be provided on the main passages and near exit doors. |  |  | 0 | 0
| Sub Total |  |  | 0 | 0 | 78010.7 | 19154.2
15 | SHOP DRAWINGS, INSPECTION AND APPROVALS |  |  | 0 | 0 | 0 | 0
a | Preparation of Shop drawings as per site conditions based the GFC drawings, the same shall be approved by client / consultant / architects. Obtaining approval from Statutory Authorities, Preparation of statutory drawings, completion Report, Arranging for Inspection, attending defects report and obtaining safety certificate from Safety Authorities for commissioning of the electrical system.(including all required statutory Norms ). Five sets as built drawings with soft copy shall be Submitted. | 1 | Job | 185000 | 5300 | 185000 | 5300
| Sub Total |  |  |  |  | 185000 | 5300
| Sub TOTAL |  |  |  |  | 7325527.52 | 1270258.42
| GRAND TOTAL(GST EXTRA) |  |  |  |  | 8595785.94

## Elec-APPROVED MAKES
LIST OF APPROVED MAKES
SL. NO. | DESCRIPTION | BRAND 1 | BRAND 2 | BRAND 3 | BRAND CONSIDERED BY THE CONTRACTOR
1 | DISTRIBUTION BOARDS | SCHNEIDER | LEGRAND/L&T/ABB | HAGER/HAVELLS
2 | MCB / ELCB/RCBO | SCHNEIDER | LEGRAND/L&T/ABB | HAGER/HAVELLS
3 | LIGHT FITTINGS | ARRAY STORM/WIPRO | REGENT/DIVINITY | PHILIPS/LT/PANASONIC
4 | LIGHT FITTINGS ( Decorative) | RIPPL Lighting /POLORIS | Radical/NEXUS | PURPLE-TURTLE/LUNARK
5 | SWITCHES & SOCKETS | LEGRAND/HONEYWELL/ANCHOR ROMA | GREATWHITE/SCHNEIDER | CRABTREE/NORTHWEST
6 | LT CABLES | POLYCAB | HAVELLS | KEI
7 | WIRES | HAVELLS/POLYCAB | POWER FLEX/ASMON | KEI/ANCHOR
8 | GLANDS | COMET | DOWELL’s
9 | TERMINAL BLOCKS | ELMAX | WAGO
10 | MCCB's | LEGRAND | SCHNEIDER / L&T | HAGER/ABB
11 | ISOLATOR / STARTERS | LEGRAND | SCHNEIDER | HAGER/ABB
12 | LT PANEL FABRICATION | CPRI APPROVED VENDORS
13 | CT/PT'S | AE | KAPPA/KALAIVANI | TRANSTECH
14 | INSTRUMENTS & PQA | EL MEASURE | RISHUB/L&T | SCHNEIDER
15 | BUS BAR SUPPORTS | POWERMAT | SARAVANA | LMAX
16 | INDICATION LAMPS (LED) | TECHNIC | L & T | ALTOS
17 | SELECTOR SWITCHES | SALZER | L & T
18 | INDUSTRIAL SOCKETS | SCAME / LEGRAND | HENSEL / MK/CAPE | MENNEKES/BALS
19 | CRIMPING SOCKETS | COMET | DOWELL’s | HEX/HMI
20 | MS CONDUITS | VIMCO | BEC / JAVERI | GUPTA (GB)
21 | PVC CONDUITS | VASIVI/ANCHOR/SUN | AVONPLAST | PRECISION
22 | GI ANODISED METAL BOX | MK | CRABTREE | LEGRAND
23 | CABLE TRAYS / RACEWAYS | OBO | PROFAB/CLASSIC/AEROSTAR | NIEDAX/JKR
24 | BALLASTS | PHILIPS | WIPRO | BAJAJ/ARRAY STORM
25 | EARTHING | ASHLOK | GRAVIN
26 | EXHAUST FANS | GEC | ALMONARD | USHA
27 | SENSORS | HONEYWELL/GRIDSENSE | LUTRON | CRESTRON
28 | EGA BOX | HONEYWELL/CONNECTWELL | MG/CJ INFRA | LEGRAND
29 | UPS System & conveters | APC/FUJI | NUMERIC/ABB | SOCOMEC/RELIO
30 | BATTERY | AMARRAJ | ROCKET | HBL

## FAS AND PA SUMMARY
FAS AND PA SUMMARY |  |  |  |  | JLL Summary
S.NO | DESCRIPTION | SUPPLY | ERECTION | TOTAL | SUPPLY | ERECTION | TOTAL
|  | AMOUNT INR | AMOUNT INR |  | AMOUNT INR | AMOUNT INR
1 | ADDRESSABLE FIRE ALARM SYSTEM | 1272964.6 | 121894.7 | 1394859.3 | 688322.395 | 90194.075 | 778516.47
2 | PUBLIC ADDRESS SYSTEM | 405110.8 | 57187 | 462297.8 | 363507.92 | 46353.8 | 409861.72
3 | SPRINKLER SYSTEM | 1113848 | 404782.2 | 1518630.2 | 1143927.6624 | 257719.92 | 1401647.5824
4 | SIGNAGE SYSTEM | 33496 | 8511.8 | 42007.8 | 23108 | 4653.4 | 27761.4
5 | FIRE EXTINGUISHER SYSTEM | 107643 | 3816 | 111459 | 107643 | 3816 | 111459
6 | ACCESS CONTROL SYSTEM | 901095.4 | 278027.4 | 1179122.8 | 701720 | 211682 | 913402
7 | CCTV SYSTEM | 474032 | 73882 | 547914 | 392624 | 39538 | 432162
8 | RODENT REPELLENT SYSTEM | 51304 | 11230.7 | 62534.7 | 23320 | 4028 | 27348
9 | WATER LEAK DETECTION SYSTEM | 58088 | 6508.4 | 64596.4 | 57293 | 6211.6 | 63504.6
10 | GAS SUPPRESSION SYSTEM | 744757.0337 | 230397.8 | 975154.8337 | 645275 | 68677.4 | 713952.4
| TOTAL WITHOUT TAX | 5162338.8337 | 1196238 | 6358576.8337 | 4146740.9774 | 732874.195 | 4879615.1724 | 1478961.6613

## FA
ADDRESSABLE FIRE ALARAM SYSTEM BOQ
SI.No | Descriptions | Unit | 1F | Total Qty | SUPPLY |  | ERECTION |  | Makes
[5 empty] | RATE INR | AMOUNT INR | RATE INR | AMOUNT INR
SITC OF ADDRESSABLE FIRE ALARM SYSTEM
1 | Analogue Addressable Intelligent 2 loop Fire alarm control panel including loop card, provision to make with a minimum capacity of 125 devices + 125 modules per loop, with battery back up for 48 Hrs during normal operation and 15 minutes alarm operation, with minimum 160 Character LCD display, necessary interface card to connect a repeater panel and all hardware & software as per specification. | Nos | 1 | 1 | 282172 | 282172 | 5300 | 5300 | NOTIFIER
2 | SITC of Bacnet card for BMS integration | Nos |  | 1 | 159000 | 159000 | 5300 | 5300 | NOTIFIER
3 | Supply Installation Testing & Commissioning of multi sensor detector (photo+heat) with base,powder coated back box and other accessories as required and Detectors shall be UL listed, - (ABOVE FALSE CEILING & FALSE FLOOR) with dust level indication | Nos | 68 | 68 | 2448.6 | 166504.8 | 265 | 18020 | NOTIFIER | 69 | 168953.4 | 18285
4 | Supply Installation Testing & Commissioning of multi sensor detector (photo+heat) with base and other accessories as required and Detectors shall be UL listed, - (BELOW FALSE CEILING)with dust level indication | Nos | 68 | 68 | 2448.6 | 166504.8 | 265 | 18020 | NOTIFIER | 69 | 168953.4 | 18285
5 | Supply Installation Testing & Commissioning of Analog Addressable Smoke Detector with programmable for timed automatic sensitivity selection with Standard base, powder coated backbox and other accessories as required and Detectors shall be UL Listed. (TRUE CEILING / ABOVE FALSE CEILING)with dust level indication | Nos | 12 | 12 | 2448.6 | 29383.2 | 265 | 3180 | NOTIFIER |  | 0 | 0
6 | Supply Installation Testing & Commissioning of Analog Addressable Smoke Detector with programmable for timed automatic sensitivity selection with Standard base and other accessories as required and Detectors shall be UL Listed. (BELOW FALSE CEILING)with dust level indication | Nos |  | 0 | 0 | 0 | 0 | 0 | NOTIFIER |  | 0 | 0
8 | Analogue Addressable Duct sensor detector with multiple sensitivity levels, programmable for timed automatic sensitivity selection and with base, UL listed,with dust level indication | Nos | 4 | 4 | 11448 | 45792 | 265 | 1060 | NOTIFIER |  | 0 | 0
10 | Supply Installation Testing & Commissioning of heat detector with base, Junction box and other accessories as required and Detectors shall be UL listed, | Nos |  | 0 | 0 | 0 | 0 | 0 | NOTIFIER |  | 0 | 0
11 | SITC of Response indicator | Nos | 59 | 59 | 90.1 | 5315.9 | 42.4 | 2501.6 | RAVEL/C SYSTEM/AGNI | 61 | 5496.1 | 2586.4
12 | Analogue Addressable Fault isolator module capable of monitoring shorted loop circuit and automatically restore communications when shorted conditions are corrected. (FIM's are used for every 20 detectors/devices) | Nos | 9.1 | 9.1 | 3127 | 28455.7 | 371 | 3376.1 | NOTIFIER | 10 | 31270 | 3710
13 | Supply, installation, fixing, testing and commissioning of Analogue Addressable Monitor module with back box(1.6mm thick RED colour) operating at 24V DC, 2A, rated at 230V, provided with DPDT contact. (FLOW SWITCH#1 BB INTEGRATION#1 WLD#2, GSS#2, FIRE DOOR#2) with required fixing accessories | Nos | 5 | 5 | 2915 | 14575 | 265 | 1325 | NOTIFIER | 8 | 23320 | 2120
14 | Supply, installation, fixing, testing and commissioning of Analogue Addressable Control module with back box (1.6mm thick RED colour) operating at 24V DC, 2A, rated at 230V, provided with DPDT contact,with required fixing accessories Access Control #1 BB INTEGRATION#1 PA INTEGRATION#1, Hooter#1 | Nos | 8 | 8 | 3354.9 | 26839.2 | 265 | 2120 | NOTIFIER | 2 | 6709.8 | 530
15 | Supply, installation, fixing, testing and commissioning of Analogue Addressable Control relay module with back box(1.6mm thick RED colour) operating at 24V DC, 2A, rated at 230V, provided with DPDT contact. with required fixing accessories, AC/FD/UPS/BAT/SERV/ELE TRIPPING | Nos | 8 | 8 | 3354.9 | 26839.2 | 265 | 2120 | NOTIFIER | 12 | 40258.8 | 3180
16 | Addressable Electronic Hooter cum Strobe ceiling mounted. The hooters shall be made of ABS plastic, and have a DB level of 65dbA and a multi tone facility. Addressable Control Module shall be fitted in a junction box. | Nos | 9 | 9 | 9010 | 81090 | 265 | 2385 | NOTIFIER | 8 | 72080 | 2120
17 | SITC of Addressable Manual call point having an integrally mounted addressable module that monitors and reports contact status. (PULL TYPE) with back box(1.6mm thick RED colour) along with required fixing accessories. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. | Nos | 9 | 9 | 4542.1 | 40878.9 | 265 | 2385 | NOTIFIER | 8 | 36336.8 | 2120
18 | 2C x 1.5 mm2, Stranded Copper conductor,Type A ST1 PVC insulated,Armoured FRLS CU Cable 1100 V as per IS 1554, with GI saddle spacers every 0.3 mtr with Single compression Cable Glands,ABS Junction Boxes (wherever required), terminals,Ferruling complete. | Rmt | 1824 | 1824 | 90.1 | 164342.4 | 26.5 | 48336 | POLYCAB / VARSHA/ KEI/DATA FLEX | 1285.95 | 115864.095 | 34077.675
19 | Supplying, installing, testing and commissioning of approved make FRLS PVC conduits on ceiling / wall / floor etc. complete with accessories like, Junction boxes, Collars, Bends, clamps, saddles etc. (for MCP) |  |  |  | 0 |  | 0 |  | VIP/ PRECISION/ASTRA/ANCHOR |  | 0 | 0
a | 25 mm dia. | Rmt | 45 | 45 | 47.7 | 2146.5 | 21.2 | 954 |  |  | 0 | 0
20 | Supply and laying of MS Powder coated Trunking 300 x 50 mm x 1.6mm with cover & fixing suppports etc as required (Cable dressing for Fire & PA panel ) | Rmt | 5 | 5 | 901 | 4505 | 148.4 | 742 | REPUTED |  | 0 | 0
21 | Supply and laying of GI enclosed raceway 300 x 50 mm x 1.6mm with cover & fixing suppports etc as required (Cable dressing inside the shaft ) | Rmt | RO | 0 | 0 |  | 0 |  | REPUTED | 8 | 0 | 0
22 | SITC of PSU for hooters & AHU tripping (inclusive of Battery ckt & battery) | Set | 3 | 3 | 9540 | 28620 | 1590 | 4770 | Battery : Panasonic/Exide/Amaron PSU : CTEC/CSYSTEM/INSYIN | 2 | 19080 | 3180
| TOTAL |  |  |  |  | 1272964.6 |  | 121894.7 |  |  | 688322.395 | 90194.075

## PA
PUBLIC ADDRESS SYSTEM BOQ
SI.No | Descriptions | Unit | 1F | Total Qty | SUPPLY |  | ERECTION |  | Makes
[5 empty] | RATE INR | AMOUNT INR | RATE INR | AMOUNT INR
1 | SITC of 6W RMS False Ceiling Mount Speakers with inbuilt 100V Line Matching Transformer, wide opening angle, optimized for music & speech applications with mounting clamps as per specifications | Nos | 68 | 68 | 848 | 57664 | 212 | 14416 | Honeywell | 64 | 54272 | 13568
2 | SITC of 6W RMS True Ceiling Mount Speakers with inbuilt 100V Line Matching Transformer, wide opening angle, optimized for music & speech applications with powder coated back box, supports as per specifications Speakers shll have the tappings at 1.5/3/6 watts | Nos | 12 | 12 | 1219 | 14628 | 212 | 2544 | Honeywell | 14 | 17066 | 2968
3 | SITC of 6 W Wall Mounted Speakers with line matching transformers as specified as per specifications | Nos | 4 | 4 | 1537 | 6148 | 212 | 848 | Honeywell | 1 | 1537 | 212
4 | SITC of System Controller complete with Microprocessor based 4 Zone Call Station, Stem Type Microphone, Dual Tone Control for Speech & Music,etc. | Nos. | 1 | 1 | 132500 | 132500 | 3180 | 3180 | Honeywell | 1 | 132500 | 3180
5 | SITC of 6 zone call station keypad with accessories | Nos. | 1 | 1 | 18550 | 18550 | 1272 | 1272 | Honeywell | 1 | 18550 | 1272
6 | SITC of Rack Mounted 120 W Power Amplifier | Nos | 1 | 1 | 26500 | 26500 | 3180 | 3180 | Honeywell | 1 | 26500 | 3180
7 | SITC of Rack Mounted 240 W Power Amplifier | Nos |  |  | 0 | 0 | 0 | 0 | Honeywell |  | 0 | 0
8 | SITC of Rack Mounted 480 W Power Amplifier | Nos | 1 | 1 | 44520 | 44520 | 3180 | 3180 | Honeywell | 1 | 44520 | 3180
9 | 2C x 1.5 mm2, Stranded Copper conductor,Type A ST1 PVC insulated,Armoured FRLS Cable 1100 V as per IS 1554, with GI saddle spacers every 0.3 mtr with Single compression Cable Glands,ABS Junction Boxes (wherever required), terminals,Ferruling complete. | Rmt. | 1008 | 1008 | 90.1 | 90820.8 | 26.5 | 26712 | POLYCAB / VARSHA/ KEI/DATA FLEX | 649.2 | 58492.92 | 17203.8
10 | SITC of Volume controller for one speaker (near reciption) | Nos | 1 | 1 | 3710 | 3710 | 265 | 265 | Heinrich/ Bosch / Honeywell |  | 0 | 0
11 | SITC OF Suitable size 9U rack as per following specification, Conforms to DIN 41494 Or Equivalent EIA/ISO/EN/CEA Standard Finish - Powder coated finish with Seven tank pretreatment process meeting ASTM standard Color - Black/off white/grey Fan module on top of the rack Welded frame with vented top cover with fan , perforated Metal Door with lock & Key and Back vented / Perforated metal door with lock & key and partially vented side panels, free standing on floor with 4 No. casters wheels with 2 no with brakes & 2 No. without brakes, cable oraginesers, Levelers with required 16A/5A power strips including accessories. Number of racks shall be as per the design requirement. vendor to consider required number of racks as per their requirement | Lot | 1 | 1 | 10070 | 10070 | 1590 | 1590 | VALL RACK / MASS RACK | 1 | 10070 | 1590
| TOTAL |  |  |  |  | 405110.8 |  | 57187 |  |  | 363507.92 | 46353.8

## FPS
FIRE PROTECTION SYSTEM BOQ
SI.No | Descriptions | Unit | 1F | Total Qty | SUPPLY |  | ERECTION |  | Makes
[5 empty] | RATE INR | AMOUNT INR | RATE INR | AMOUNT INR
SPRINKLER SYSTEM:
1 | Supplying, installing,hydraulic testing and commissioning of Heavy grade MS Pipes confirming to IS :1239 part - I with malleable specials confirming to IS:1239 part - II, such as Tees, elbows, check nuts, unions, flanges, nipples etc. Including cutting, fixing in / on walls / on Floors, ceiling by using suitable supports such as MS channels ,angles,flats,rods as required at site with anchor fasteners,clamps,threaded rods,nuts,bolts,washers etc...complete. Painting the exposed with one coat of metal zinc chromate primer with two coats of synthetic enamel paint of approved colour / shade etc., complete.The pipe fittings shall be welded type up to 50 mm dia and grooved type for 65 mm dia & above. | [7 empty] | PIPE:JINDAL STAR / TATA SOCKET FITTINGS: B&M/ VS/ BHARATH FORGE
a | 25mm nominal dia | Rmt | 360 | 360 | 445.2 | 160272 | 148.4 | 53424 |  | 312.5 | 139125 | 46375
b | 32mm nominal dia | Rmt | 56 | 56 | 572.4 | 32054.4 | 180.2 | 10091.2 |  | 56.5 | 32340.6 | 10181.3
c | 40mm nominal dia | Rmt | 48 | 48 | 699.6 | 33580.8 | 212 | 10176 |  | 49.4 | 34560.24 | 10472.8
d | 50mm nominal dia | Rmt | 56 | 56 | 901 | 50456 | 296.8 | 16620.8 |  | 55.8 | 50275.8 | 16561.44
e | 65mm nominal dia | Rmt | 54 | 54 | 2094.666 | 113111.964 | 339.2 | 18316.8 |  | 63.9 | 133849.1574 | 21674.88
f | 80mm nominal dia | Rmt | 48 | 48 | 2416.8 | 116006.4 | 477 | 22896 |  | 52.2 | 126156.96 | 24899.4
g | 100mm nominal dia | Rmt | 18 | 18 | 3403.872 | 61269.696 | 583 | 10494 |  | 24 | 81692.928 | 13992
h | 150mm nominal dia | Rmt | 36 | 36 | 4199.19 | 151170.84 | 901 | 32436 |  | 44.3 | 186024.117 | 39914.3
[5 empty] | 0 |  | 0
2 | Supply testing and commissioning of 15 mm gunmetal/chrome quartzoid bulb, quick response sprinkler heads suitable for 68 deg. C, K 80 |  |  |  | 0 |  | 0 |  | TYCO/ VIKING/ VICTUALIC
| a) Pendent- 68deg C | Nos | 195 | 195 | 254.4 | 49608 | 132.5 | 25837.5 |  | 193 | 49099.2 | 25572.5
| a) Pendent- 79deg C | Nos |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
| b) Upright - 68deg C | Nos | RO | 0 | 0 | 0 | 0 | 0 |  | 34 | 0 | 0
| c)Upright - 79deg C | Nos |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
3 | Dial type pressure guage for (0-16 Kg/cm2) with necessary nipple & other fittings, mounting arrangements and with a 15 mm ball valve | Nos | 1 | 1 | 1749 | 1749 | 174.9 | 174.9 | H. GURU / WAREE / FIEBIG | 1 | 1749 | 174.9
4 | Supply, Installation, Testing & Commissioning of 25mm Ball valve with sight glass for Sprinkler test line | Nos |  | 0 | 0 | 0 | 0 | 0 | ZOLOTO/ LEADER/ LB |  | 0 | 0
5 | Supply, Installation, Testing & Commissioning of 25mm Ball valve with sprinkler bulb for Sprinkler test line | Nos | 1 | 1 | 1961 | 1961 | 159 | 159 | ZOLOTO/ LEADER/ LB |  | 0 | 0
6 | Supply, Installation, Testing & Commissioning of 50mm Ball valve for Sprinkler drain line | Nos | 1 | 1 | 2332 | 2332 | 159 | 159 | ZOLOTO/ LEADER/ LB |  | 0 | 0
7 | Supply, Installation, Testing & Commissioning of Flow Switches with two NO and two NC contacts with necessary nipple & other fittings, Flow switch shall be suitable for 150 dia | Nos | 1 | 1 | 6890 | 6890 | 848 | 848 | SYSTEM SENSOR/ HONEYWELL/ POTER | 1 | 6890 | 848
8 | Providing and fixing C.I. butterfly valves to IS:13095 with operating lever, bolts, nuts, washers and companion flanges complete. (PN-16) |  |  | 0 | 0 |  | 0 |  | AUDCO/ KEYSTONE/ INTTERVALVE |  | 0 | 0
a | 50mm dia | Nos | RO | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
b | 80mm dia | Nos | RO | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
c | 100mm dia | Nos | RO | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
d | 150mm dia | Nos | 1 | 1 | 9010 | 9010 | 848 | 848 |  |  | 0 | 0
9 | Supply, installation, testing & commissioning of Non Return Valve of 150mm dia IS:5312( PN 16) along with connection flanges, bolts / nuts etc. | Nos |  | 0 | 0 | 0 | 0 | 0 | INTERVALVE / ADUCO / ZOLOTO |  | 0 | 0
10 | Supply & fixing of approved type rosette plates ( Recessed type, in two piece) for Sprinklers below false ceiling area. |  |  | 0 | 0 |  | 0 |  | FABRICATED(SAMPLE APPROVAL TO BE TAKEN) |  | 0 | 0
a | The Rosette shall be fabricated by M.S. plate of 2mm thick and the finish shall be powder coated and color shall be as approved by architects / clients. | Nos | 195 | 195 | 81.62 | 15915.9 | 31.8 | 6201 |  | 193 | 15752.66 | 6137.4
11 | Stainless steel corrugated flexible pipe(hose) for dropping sprinklers below false ceiling, pipe shall be UL Listed, 16 bar pressure rating and 1800 mm long 25 mm dia with union / reducer collar, clamps etc. as required. (BRAIDED) | Nos | 0 | 0 | 0 | 0 | 0 | 0 | TYCO/ VIKING/ VICTUALIC |  | 0 | 0
12 | Stainless steel corrugated flexible pipe(hose) for dropping sprinklers below false ceiling, pipe shall be UL Listed, 16 bar pressure rating and 1500 mm long 25 mm dia with union / reducer collar, clamps etc. as required. (BRAIDED) | Nos | 195 | 195 | 1484 | 289380 | 212 | 41340 | TYCO/ VIKING/ VICTUALIC | 193 | 286412 | 40916
13 | Stainless steel corrugated flexible pipe(hose) for dropping sprinklers below false ceiling, pipe shall be UL Listed, 16 bar pressure rating and 1000 mm long 25 mm dia with union / reducer collar, clamps etc. as required.(BRAIDED) | Nos | RO | 0 | 0 | 0 | 0 | 0 | TYCO/ VIKING/ VICTUALIC |  | 0 | 0
14 | Air Release Valve - 15mm | Nos | RO | 0 | 0 | 0 | 0 | 0 | ZOLOTO / NEWAGE / HAWA |  | 0 | 0
15 | Removing of existing Upright sprinkler from the existing location and refixing the same in proposed location with required accessories. | Nos | 40 | 40 | 0 | 0 | 318 | 12720 |  |  | 0 | 0
16 | Testing & commissioning of sprinkler system 24hr at 12 bar pressure for both existing and new pipes | Lot | 1 | 1 | 0 |  | 21200 | 21200 |  |  | 0 | 0
17 | Removing of exisiting Pendent sprinklers from the existing sprinkler network and refixing the same on the proposed/same location. necessary costing for removing,welding(if required), refixing to be included in cost. (vendor is responsible for safe handling of sprinklers, if any damage occurs during removing , same shall be procured by vendor and install without extra cost) | Nos | 20 | 20 | 0 |  | 901 | 18020 |  |  | 0 | 0
18 | Cutting , removing, rerouting / providing dummy of existing fire fighting pipes, sizes from 25 to 150mm dia from various places or reroute the existing pipes as per the site requirement ( SERVER ROOM/UPS & BATTERY ROOM) Vendor to visit the site, analyse the quantum of works involved & quote accordingly and also refer the layout | Lot | 1 | 1 | 0 |  | 90100 | 90100 |  |  | 0 | 0
19 | Painting of existing pipes where ever modification done | Lot | 1 | 1 | 19080 | 19080 | 12720 | 12720 | ASIAN/ BERGER/ NIPPON |  | 0 | 0
20 | Modification in existing sprinkler network as per the drawing attached Work involves cutting the existing entier branch from main header and relocate as per the drawing item shall inclusive of removing the existing branch with bulbs and refixing the same with required supports. | Lot |  | 0 | 0 |  | 0 | 0
| TOTAL |  |  |  |  | 1113848 |  | 404782.2 |  |  | 1143927.6624 | 257719.92

## SIGNAGE
SIGNAGE SYSTEM BOQ
SI.No | Descriptions | Unit | 1F | Total Qty | SUPPLY |  | ERECTION |  | Makes
[5 empty] | RATE INR | AMOUNT INR | RATE INR | AMOUNT INR
1 | " FIRE EXIT " (AUTOGLOW) - SINGLE SIDE - FOR FIRE EXIT DOORS - 150*300mm | Nos | 1 | 1 | 371 | 371 | 137.8 | 137.8 | PROLITE/AUTOGLOW/BRIGHTONICS
2 | ""DIRECTIONAL EMERGENCY EXIT " (AUTOGLOW) - DOUBLE SIDE - 150*300mm - FOR INTERNAL AREAS | Nos | 32 | 32 | 371 | 11872 | 137.8 | 4409.6 | PROLITE/AUTOGLOW/BRIGHTONICS
3 | " EXTINGUISHER Signages - Autoglow, with suspension chains (Autoglo signages, size 150 x 300) - double side with suspension chains (SS) | Nos | 14 | 14 | 371 | 5194 | 137.8 | 1929.2 | PROLITE/AUTOGLOW/BRIGHTONICS | 20 | 7420 | 2756
4 | " MCP Signages - Autoglow, with suspension chains (Autoglo signages, size 150 x 300 - double side with suspension chains (SS) | Nos | 9 | 9 | 371 | 3339 | 137.8 | 1240.2 | PROLITE/AUTOGLOW/BRIGHTONICS | 8 | 2968 | 1102.4
5 | Fire Evacuation Route Map as per following specification Preparation of drawing and providing, Autoglow Fire escape route map in clear acrylic glass and required glass studs supports etc. Indicating direction, Key plan, contact numbers etc. (The sample of the same need to be presented for approval before execution)…. (Maximum size of the board A3) Evacuation plan shall be glow in dark. A3 size with 5mm thick rear & 3mm thick front acrylic cover including wall mount supports. | Nos | 3 | 3 | 4240 | 12720 | 265 | 795 | PROLITE/AUTOGLOW/BRIGHTONICS | 3 | 12720 | 795
| TOTAL |  |  |  |  | 33496 |  | 8511.8 |  |  | 23108 | 4653.4

## FE
FIRE EXTINGUISHER SYSTEM BOQ
SI.No | Descriptions | Unit | 1F | Total Qty | SUPPLY |  | ERECTION |  | Makes
[5 empty] | RATE INR | AMOUNT INR | RATE INR | AMOUNT INR
SITC OF FIRE EXTINGUISHER
1 | CO2 type Fire Extinguisher ISI marked confirming to IS:15683 latest. Capacity 4.5 Kg. Complete with delivery hose horn, squeeze grip release valve, locking arrangement,operating temperature -30°C to +55°C, supplied with body bearing IS 7285 mark and approved by CCoE tested at 250 kgf/cm2., fitted with ISI marked & CCoE approved valve as per IS 3224. CO2 Gas as per IS: 15222. externally painted with PO Red Shade No. 538 of IS 5, operation manual and floor stand or Wall Mount Bracket including accessories as required as per site condition | Nos | 14 | 14 | 5909.5 | 82733 | 159 | 2226 | KANEX/CEASEFIRE/MINIMAX | 14 | 82733 | 2226
2 | Powder Fire Extinguisher (Stored Pressure type) (Powder pressurized with dry nitrogen gas at 15 bar.) capacity: 6kg duly ISI marked conforming to IS: 15683:2006/latest, with IS 14609 ISI marked ABC powder complete with squeeze grip release valve, discharge pipe, locking arrangement, pressure gauge, operation manual,Body Hydrotested at 35 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, and floor stand or Wall Mount Bracket including accessories as required as per site condition | Nos | 10 | 10 | 2491 | 24910 | 159 | 1590 | KANEX/CEASEFIRE/MINIMAX | 10 | 24910 | 1590
3 | Wet chemical stored pressure 6Ltr capacity including accessories, pressure guage and floor mounting accessories (kitchen - preparation area) | Nos |  | 0 |  | 0 |  | 0 | KANEX/CEASEFIRE/MINIMAX
4 | FE36 Automatic ceiling Mounted Clean agent Extinguisher - 5 Kg with Ceiling mount accessories including nozzle(57 deg), pressure guage. ISI approved - batttery (1) | Nos |  | 0 |  | 0 |  |  | KANEX/CEASEFIRE/MINIMAX
| TOTAL |  |  |  |  | 107643 |  | 3816 |  |  | 107643 | 3816

## ACCESS
ACCESS CONTROL SYSTEM
SI.No | Descriptions | Unit | 1F | Total Qty | SUPPLY |  | ERECTION |  | Makes
[5 empty] | RATE INR | AMOUNT INR | RATE INR | AMOUNT INR
1 | Supply, Installation, Testing and Commssioining of 2 reader controller, power supply unit, TCP IP connectivity with tamper detection provision as per the tender specifications.Cost shall inclusive of enclosure and power supply unit for controller/EM locks (power supply unit shall inclusive of battery backup 8 hrs). Controller Should Support global Antipass back. | Nos | 7 | 7 | 23850 | 166950 | 2120 | 14840 | SPECTRA | 7 | 166950 | 14840
2 | Supply, installation, testing & commissioning of Smart card readers with 2.5mm thick SS front plate as per specification suitable for mounting on metal surface/metal frames or wooden frames wall or as required based on site conditions including all accessories. | Nos | 10 | 10 | 9010 | 90100 | 424 | 4240 | SPECTRA | 10 | 90100 | 4240
3 | Supply, Installation, Testing and Commssioining of Biometric with card Reader as per specification suitable for mounting on metal surface/metal frames or wooden frames wall or as required based on site conditions including all accessories. | Nos | 4 | 4 | 35510 | 142040 | 2650 | 10600 | SPECTRA | 4 | 142040 | 10600
4 | Supply, installation, testing and commissioning of Smart Access Cards with Lanyard to hold the cards as per specification. | Nos | 200 | 200 | 206.7 | 41340 | 0 | 0 | HID | 200 | 41340 | 0
5 | Supply, Installation, Testing and Commssioining of Electromagnetic Lock with required mounting brackets for single door as per the tender specifications | Nos | 7 | 7 | 2756 | 19292 | 424 | 2968 | Bell, SDC, ASSA ABLOY | 7 | 19292 | 2968
6 | Supply, Installation, Testing and Commssioining of Electromagnetic Lock with required mounting brackets for double door as per the tender specifications | Nos | 0 | 0 | 0 | 0 | 0 | 0 | Bell, SDC, ASSA ABLOY |  | 0 | 0
7 | Supply, Installation, Testing and Commssioining of surface / flush mounted (as required at site) Magnetic Contact (Door position sensor) for access controlled doors as per the tender specifications | Nos | 7 | 7 | 371 | 2597 | 106 | 742 | Sentrol, Secoalarm, Ademco | 7 | 2597 | 742
8 | Supply,Installation, Testing and Commssioining of the Security Management Server software and liscence also proivde Integrated Access Management 1 Master Software for Access Control monitoring as per the tender specifications Vendor shall consider as per OEM recommendations. | Nos | 1 | 1 | 0 | 0 | 143100 | 143100 | SPECTRA | 1 | 0 | 143100
9 | Supply, Installation, Testing and Commssioining of security Management Software PC Server Station with minimum Intel i8 3.1 Ghz processor, 16 GB RAM, Graphics card with 1GB, 500 GB HDD, 24" Color flat panel LED Monitor,500TVL, 1080P HD Resolution, 100/1000Mbps network card with original Microsoft Windows 8 Operating System or higher, antivirus softwares,MS softwares.Vendor shall consider as per OEM recommendations These PC (1#) will be loaded with Security Management Server software Master Software, Access Control & Alarm Monitoring | Nos | 1 | 1 | 116600 | 116600 | 4770 | 4770 | Lenovo/ Dell/ Samsung | 1 | 116600 | 4770
10 | Supply, Installation, Testing and Commssioining of Local scare alarm with required wiring between LCA & door contacts (For fire exit doors). Rate shall inclusive of door contacts | Nos | 1 | 1 | 2862 | 2862 | 1060 | 1060 | LSA:C SYSTEM/INSYIN |  | 0 | 0
11 | Supply, Installation, Testing and Commssioining of panic bar for fire exit doors (Single leaf) as per Specification (For fire exit doors, panic BAR shall be RED in color). | Nos | 1 | 1 | 19080 | 19080 | 1590 | 1590 | PANIC BAR:DORMA |  | 0 | 0
12 | Supply, Installation, Testing and Commssioining of panic bar for fire exit doors (double leaf) as per Specification (For fire exit doors, Panic BAR shall be RED in color). | Nos | 0 | 0 | 0 | 0 | 0 | 0 | PANIC BAR:DORMA |  | 0 | 0
13 | Supply and laying of 4 core 1.0 Sq mm Un Armoured Shielded, Multistanded Copper Conductor, PVC sheathed Cable with accessories for connecting controller to Lock & door position sensors, Buzzer,BGU,Pushbutton as per the tender specifications | Rmt | 960 | 960 | 84.8 | 81408 | 26.5 | 25440 | Varsha / Ravicab / Deepanjan | 504 | 42739.2 | 13356
14 | Supply and laying of 8 core x 1 Sq mm Un Armoured Shielded, Multistanded Copper Conductor, PVC sheathed Cable with accessories for connecting controller to readers as per the tender specifications | Rmt | 800 | 800 | 127.2 | 101760 | 26.5 | 21200 | Varsha / Ravicab / Deepanjan | 504 | 64108.8 | 13356
15 | Supply and laying of 2 core x 1 Sq mm Un Armoured Shielded, Multistanded Copper Conductor, PVC sheathed Cable with accessories | Rmt |  | 0 | 0 |  | 0 |  | Varsha / Ravicab / Deepanjan |  | 0 | 0
16 | Supply and laying of CAT6 UTP 23AWG solid Unarmoured POE cable Cable shall inclusive of connectors, patch chord and complete with crimping. The cable shall be considered with connectors on both th ends inclusive of necessary accessories | Rmt | 84 | 84 | 47.7 | 4006.8 | 15.9 | 1335.6 | MOLEX / D Link |  | 0 | 0
17 | Supply and laying of 1" - 2 mm thick FRLS - PVC Conduits,JB's in wall, columns, ceiling etc., including associated civil works | Rmt | 1844 | 1844 | 42.4 | 78185.6 | 21.2 | 39092.8 | VIP / AVANPLAST / ISI Marked equivalent |  | 0 | 0
18 | Supply, Installation, Testing and Commissioning of Buzzer for access controlled doors as specified in the Tender Specifications | Rmt | 7 | 7 | 1272 | 8904 | 265 | 1855 | VAISHNO /LOTO | 7 | 8904 | 1855
19 | Supply installation, testing, commissioning of EDR (EMERGENCY BREAK GLASS ) | Rmt | 7 | 7 | 1007 | 7049 | 265 | 1855 | MAG/AUTO COP/ALAGAT/Agni | 7 | 7049 | 1855
20 | Supply installation, testing, commissioning of Egress Switch Units with back box and accessories | Rmt |  | 0 | 0 | 0 | 0 | 0 | KAC, Europlex, Sentrol, Honeywell |  | 0 | 0
21 | Supply installation, testing, commissioning of back box | Nos |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
22 | Supply and laying of MS Powder coated Trunking 300 x 50 mm x 2mm with cover & fixing suppports etc as required for panel dressing | Mtrs | 21 | 21 | 901 | 18921 | 159 | 3339 | LOCAL APPROVED |  | 0 | 0
23 | 16 port 10/100/1000 layer 2 , LAN switches with IP multicast snooping and data-driven IGMP support and with minimum two 1000baseT RJ45 uplink ports and two 1000 baseT Fiber uplink ports, patch cords, patch panel and enclosure/rack for switch with mounting supports and all accessories. | Nos | R0 | R0 | 0 | 0 | 0 | 0 | D-Link,TP Link,Netgear |  | 0 | 0
| TOTAL |  |  |  |  | 901095.4 |  | 278027.4 |  |  | 701720 | 211682

## CCTV
IP CCTV SYSTEM
SI.No | Descriptions | Unit | 1F | Total Qty | SUPPLY |  | ERECTION |  | Makes
[5 empty] | RATE INR | AMOUNT INR | RATE INR | AMOUNT INR
1 | IP based IR Dome Indoor Camera: Supply, Installation, Testing & Commissioning of IP Network TDN, IR Dome Camera, 1/3" 2 MP CMOS , 2 MP @25fps or better , triple stream, Min. Illumination required 0.002ux/F1.5(color, 30IRE) 0Lux/F1.5(IR on), 120dB True WDR, Min. Pixels 1920 × 1080 (2 MP), 2.7mm~13.5mm, MFZ, motorized focus lens Backlight Compensation, Audio Input/Output, Alarm IN/OUT, 3DNR, Privacy Mask, 256GB SD Card support, IR Distance with upto 40m, with inbuilt analtycis Motion Detection, Video Tampering, Scene Changing, Tripwire Intrusion, Compression Technolgy H.265 / H.264 / Smart Codec / MJPEG, 128GB SD card support, IP67 , IK10+B1 , PoE, H.264, MJPEG, PoE IEEE 802.3af Class 0, 12 VDC, Die-Cast Aluminium Construction, Having Operating temp range : –30°C to 60° C. Certifications: ONVIF Profile S, G, Q, T compliant, UL, CE, FCC,EN compliant. Required wall / ceiling mounting accessories as specified in the Tender Specifications . The camera shall be capable of operating on POE/12VDC/24VAC . The camera shall be certified with CE, FCC, UL and ROHS certifications. Camera shall be supplied along with Suitable adaptor with 3 meter cable and suitable mounting support/back box/MS powder coated pole for suspended cameras. Upto 20 meter Coverage | Nos | 30 | 30 | 3710 | 111300 | 795 | 23850 | Honeywell | JLL Considered Model : HONEYWELL - I-HIE2PI-EL | 30 | 111300 | 23850
2 | SITC of Network Video Recorder: Supply , Installation , Testing and commissioning of 16 Channel NVR (Network Video Recorder), Up to 8-ch IP cameras can be connected, Incoming Bandwidth 320 Mbps, , SATA Hard Disks with interfaces, ANR Technology, H.265/H.264/MPEG4 video compression, 3 × USB at least 1 × USB with 3.0, upport H.265, MJPEG,Supports RAID0, RAID1, RAID5, RAID6 and RAID10 ,Supports HDD hot swap, Supports Dual Power-Redundant, Alarm I/O 16/4, RS-485, RS-232, 2 RJ-45 10 /100/1000 Mbps self-adaptive Ethernet interface, Multiple network monitoring: Web viewer, CE, FCC, UL certified, including fixing accessories and cable termination with required connectors/Jack, complete in all respect as per instruction of engineer in-charge. Storage to be considered at 720P, 15FPS, 60days Storage and 70% motion based recording . HDD Calculation to be submitted & should be approved by consultant. Rate shall be inclusive of required survveillance hard disk (make: Seagate, Western digital) | Nos | R0 | 0 | 0 | 0 | 0 | 0 | Honeywell |  |  | 0 | 0
3 | SITC of Network Video Recorder: Supply , Installation , Testing and commissioning of 32 Channel NVR (Network Video Recorder), Up to 32-ch IP cameras can be connected, Incoming Bandwidth 320 Mbps, , SATA Hard Disks with interfaces, ANR Technology, H.265/H.264/MPEG4 video compression, 3 × USB at least 1 × USB with 3.0, upport H.265, MJPEG,Supports RAID0, RAID1, RAID5, RAID6 and RAID10 ,Supports HDD hot swap, Supports Dual Power-Redundant, Alarm I/O 16/4, RS-485, RS-232, 2 RJ-45 10 /100/1000 Mbps self-adaptive Ethernet interface, Multiple network monitoring: Web viewer, CE, FCC, UL certified, including fixing accessories and cable termination with required connectors/Jack, complete in all respect as per instruction of engineer in-charge. Storage to be considered at 720P, 15FPS, 90days Storage and 70% motion based recording . HDD Calculation to be submitted & should be approved by consultant. Rate shall be inclusive of required survveillance hard disk (make: Seagate, Western digital) | Nos | 1 | 1 | 97944 | 97944 | 5300 | 5300 | Honeywell | JLL Considered Model : HONEYWELL - I-HNVR-1240 | 1 | 97944 | 5300
3 | Supply, Installation, Testing and Commssioining of Monitoing PC Station with the following specification Intel i8 3.4 Ghz processor, 16GB RAM Graphics card with 2GB, 1000 GB HDD, Dual HDMI Output, 4USB ports, 100/1000Mbps network card with original Microsoft Windows 10 Operating System, antivirus softwares,MS softwares,Wire less Keyboard & Mouse etc.or If the above specification is not match the vendor requirement. request vendor to consider as per OEM recommendation | Nos | 1 | 1 | 116600 | 116600 | 4770 | 4770 | Lenovo/ Dell/ Samsung |  | 1 | 116600 | 4770
4 | Supply, Installation, Testing and Commssioining of min 40" LED TV with 24" diagonal screen size, Contrast ratio min. 6000:1, Native Resolution : 1080P FULL HD Aspect ration- 16:9, color system - PAL/NTSC, Data signals - 2#HDMI,VGA,2#USB, SVGA, XGA, S-Video input, inbuilt speakers, required nos of HDMI cables for connectivity, wall mount kit with PC Connectivity for Multi screen video display and with anti reflectiver screen coating. TV shall be industrial grade and suitable for 24/7 operation. | Nos | 1 | 1 | 47700 | 47700 | 3710 | 3710 | Lenovo/ Dell/ Samsung |  | 1 | 47700 | 3710
5 | SITC OF12U RACKS for CCTV Equipments as per following specification, Conforms to DIN 41494 Or Equivalent EIA/ISO/EN/CEA Standard Finish - Powder coated finish with Seven tank pretreatment process meeting ASTM standard Color - Black/off white/grey Fan module Mount Provision on top Cover Welded frame with vented top cover with fan mounting provision, Associated Front Glass or perforated Metal Door with lock & Key and Back vented / Perforated metal door with lock & key and partially vented side panels, free standing on floor with 4 No. casters wheels with 2 no with brakes & 2 No. without brakes, cable oraginesers, Levelers with required 16A/5A power strips including accessories. Number of racks shall be as per the design requirement for switches locations and main cctv equipents. vendor to consider required number of racks as per their requirement | Lot | 1 | 1 | 19080 | 19080 | 1908 | 1908 | Netrack/Val rack/equivalent |  | 1 | 19080 | 1908
6 | POE SWITCHES, CABLING, CABLE TRAY and CONDUITS |  |  |  | 0 |  | 0 |  |  |  |  | 0 | 0
7 | 8 port 10/100/1000 layer 2 , POE switches with IP multicast snooping and data-driven IGMP support and with minimum two 1000baseT RJ45 uplink ports and two 1000 baseT Fiber uplink ports, patch cords, patch panel and enclosure/rack for switch with mounting supports and all accessories. | Nos | R0 | 0 | 0 | 0 | 0 | 0 | D-Link,TP Link,Netgear |  |  | 0 | 0
8 | 32 port 10/100/1000 layer 2 , POE switches with IP multicast snooping and data-driven IGMP support and with minimum two 1000baseT RJ45 uplink ports and two 1000 baseT Fiber uplink ports,patch cords, patch panel and enclosure/rack for switch with mounting supports and all accessories. | Nos | R0 | 0 | 0 | 0 | 0 | 0 | D-Link,TP Link,Netgear |  |  | 0 | 0
9 | Supply and laying of CAT6 UTP 23AWG solid Unarmoured POE cable Cable shall inclusive of connectors, patch chord and complete with crimping. The cable shall be considered with connectors on both th ends inclusive of necessary accessories | Mtrs | 1200 | 1200 | 33.92 | 40704 | 15.9 | 19080 | COMMSCOPE/MOLEX |  |  | 0 | 0
10 | Supply and laying of 1" - 2 mm thick FRLS - PVC Conduits,JB's in wall, columns, ceiling etc., including associated civil works | Mtrs | 960 | 960 | 42.4 | 40704 | 15.9 | 15264 | ANCHOR/VIP/PRECISION |  |  | 0 | 0
| TOTAL |  |  |  |  | 474032 |  | 73882 |  |  |  | 392624 | 39538

## RODENT
RODENT REPELLENT SYSTEM BOQ
SI.No | Descriptions | Unit | SERVER ROOM | UPS ROOM | BATTERY ROOM | Total Qty | SUPPLY |  | ERECTION |  | Makes
[7 empty] | RATE INR | AMOUNT INR | RATE INR | AMOUNT INR
1 | Supply, Installation, Testing and Commissioning of Master Console panel including support bracket (12 TRANSDUCER PER CONSOLE) with modbus for BMS integration | Nos | 1 | 1 |  | 2 | 8480 | 16960 | 1060 | 2120 | Rscat,Csystems | 2 | 16960 | 2120
2 | SITC of Transducer capable of Emitting Ultrasonic sound of frequencies 20 Khz and higher, with blinking LED Indication & shall capable to covering area of 150 Sq ft in floor & ceiling void and 300Sqft in Room void. Rate shall inclusive of MS backbox | Nos | 3 | 3 | 3 | 9 | 636 | 5724 | 159 | 1431 | Rscat,Csystems | 9 | 5724 | 1431
3 | SITC of 1 pair flexible 14/40 SWG Specially coated wire, PVC sheathed Cable | Mtrs | 45 | 45 | 45 | 135 | 21.2 | 2862 | 15.9 | 2146.5 | Rscat,Csystems or recommended by manufacturer | 30 | 636 | 477
4 | Supply and surface laying of 25mm dia 2mm thick PVC FRLS Conduit with GI Saddels and spacers at every 0.3 meter | Mtrs | 45 | 45 | 45 | 135 | 42.4 | 5724 | 21.2 | 2862 | BEC/GB |  | 0 | 0
5 | Supply and laying of MS Powder coated Trunking 300 x 50 mm x 1.6mm with cover & fixing suppports etc as required (Cable dressing) | Mtrs | 6 | 6 | 6 | 18 | 1113 | 20034 | 148.4 | 2671.2 | REPUTED |  | 0 | 0
| TOTAL | [6 empty] | 51304 |  | 11230.7 |  |  | 23320 | 4028

## WLD
WATER LEAK DETECTION SYSTEM BOQ
SI.No | Descriptions | Unit | SERVER ROOM | UPS ROOM | UPS ROOM | Total Qty | SUPPLY |  | ERECTION |  | Makes
[7 empty] | RATE INR | AMOUNT INR | RATE INR | AMOUNT INR
1 | Water Leak Detection sensing cables with end of line connectors along with Hold-down clips at every 1M interval. | Mtrs | 20 | 20 | 20 | 60 | 562.86 | 33771.6 | 31.8 | 1908 | Synopsys ,Csystems | 60 | 33771.6 | 1908
2 | 4 ZONE Water leak detection panel including battery backup (12 hr) as per the below specification inclusive of all necessary accessories Inbuilt with Modbus for BMS integration Relay output for Alarm and fault 230V AC 5A LED Indications (power ON, Alarm, fault etc) 100 event log wall mount type with enclosure and PSU with battery backup | Nos | 1 | 1 |  | 2 | 10070 | 20140 | 1590 | 3180 | Synopsys ,Csystems | 2 | 20140 | 3180
3 | Sounder - 75 db @ 1 mtr | Nos | 1 | 1 |  | 2 | 895.7 | 1791.4 | 265 | 530 | RAVEL / REPUTED | 2 | 1791.4 | 530
3 | 2C x 1.5 mm2, Stranded Copper conductor,Type A ST1 PVC insulated, Armoured FRLS Cable 1100 V as per IS 1554, with GI saddle spacers every 0.3 mtr with Single compression Cable metal Glands, MS POWDER COATED Junction Boxes (wherever required), terminals, Ferruling complete. | Mtrs | 15 | 15 |  | 30 | 79.5 | 2385 | 29.68 | 890.4 | POLYCAB / VARSHA/ KEI/DATA FLEX | 20 | 1590 | 593.6
| TOTAL WITHOUT TAX | [6 empty] | 58088 |  | 6508.4 |  |  | 57293 | 6211.6

## GSS
GAS SUPPRESSION SYSTEM WORKS BOQ
S.NO | DESCRIPTION | UNIT | Server room | UPS&BATTERY room | Total | SUPPLY |  | ERECTION |  | MAKES
[6 empty] | RATE INR | AMOUNT INR | RATE INR | AMOUNT INR
1 | 80 Lt FK 5-1-12 (Fluoro Ketone) approved Cylinder assembly | Nos | 1 | 1 | 2 | 90100 | 180200 | 5300 | 10600 | TYCO/UTC/HONEYWELL/CRYPTZO | 2 | 180200 | 10600
2 | 120 Lt FK 5-1-12 (Fluoro Ketone) approved Cylinder assembly | Nos |  |  | 0 | 0 | 0 | 0 | 0 | TYCO/UTC/HONEYWELL/CRYPTZO |  | 0 | 0
3 | Pressure Guage +Low pressure supervisory switch | NOS | 1 | 1 | 2 | 16536 | 33072 | 636 | 1272 |  | 2 | 33072 | 1272
4 | Agent - FK 5- 1- 12 (Fluoro Ketone) - FK 1230® | Kgs | 30.4568 | 39.8281 | 70.2849 | 2385 | 167629.4337 | 0 | 0 | TYCO/UTC/HONEYWELL/CRYPTZO | 71 | 169335 | 0
5 | Electromagnetic Actuator | NOS | 1 | 1 | 2 | 28408 | 56816 | 530 | 1060 |  |  | 0 | 0
6 | Manual Actuator | NOS | 1 | 1 | 2 | 3858.4 | 7716.8 | 275.6 | 551.2 |  | 2 | 7716.8 | 551.2
7 | Pneumatic actuator | NOS | 1 | 1 | 2 | 7314 | 14628 | 275.6 | 551.2 |  |  | 0 | 0
8 | SITC of Flexible Discharge Hose with NRV for cylinders | NOS | 1 | 1 | 2 | 20670 | 41340 | 530 | 1060 |  | 2 | 41340 | 1060
9 | Flexible Actuation Hose with ELBOW/TEE connector & adopter kit | NOS | 1 | 1 | 2 | 5088 | 10176 | 318 | 636 |  |  | 0 | 0
10 | SITC of Nozzles, 360 Deg / 180 Deg Throw, selection as per approved hydraulic flow calculations. | NOS | 3 | 6 | 9 | 3604 | 32436 | 318 | 2862 |  | 9 | 32436 | 2862
11 | Wall mount kit for ABOVE cylinders | Lot | 1 | 2 | 3 | 2120 | 6360 | 318 | 954 |  |  | 0 | 0
12 | SITC of Warning Plate "THIS ROOM IS PROTECTED BY NOVEC1230" (for use outside room) | NOS | 1 | 1 | 2 | 2120 | 4240 | 159 | 318 |  | 4 | 8480 | 636
13 | SITC of Warning Plate "THIS ROOM IS PROTECTED BY NOVEC1230" (for use inside room) | NOS | 1 | 1 | 2 | 2120 | 4240 | 159 | 318 |  |  | 0 | 0
14 | SITC of NOVAC Piping, Sch 40 MS Seamless ; ASTM A106 Gr B, as per flow calculations for the specific hazard volume. Including necessary pressure tests for pipes | LOT | 1 | 1 | 2 | 25440 | 50880 | 15900 | 31800 | TATA / JINDAL | 2 | 50880 | 31800
15 | SITC of Manual Abort Station | NOS | 2 | 2 | 4 | 1060 | 4240 | 212 | 848 | RAVEL | 4 | 4240 | 848
16 | SITC of Manual Gas Release Station (Multi action) | NOS | 2 | 2 | 4 | 1060 | 4240 | 212 | 848 | RAVEL | 2 | 2120 | 424
17 | SITC of Gas Release and builtin conventional fire alarm panel (CE APPROVED)With monitored Power supply and FittingsPower supply units shall be with battery backup of 12hrs for gas release panel & Hooter | NOS | 1 | 1 | 2 | 22260 | 44520 | 2120 | 4240 | RAVEL, | 2 | 44520 | 4240
18 | SITC of Smoke cum Heat Detector | NOS | 3 | 6 | 9 | 1007 | 9063 | 265 | 2385 | RAVEL, | 9 | 9063 | 2385
19 | SITC of Response Indicator | NOS | 2 | 4 | 6 | 90.1 | 540.6 | 42.4 | 254.4 | RAVEL, C SYSTEM | 6 | 540.6 | 254.4
20 | SITC of Manual Call point | NOS | 2 | 2 | 4 | 1033.5 | 4134 | 318 | 1272 | RAVEL, |  | 0 | 0
21 | SITC of 24 VDC operated Signages for "Evacuation" and "No entry" inside and outside the protected enclosure, 1 no. each type for every room. Shall be Powered from Gas Release Panel. | SET | 1 | 1 | 2 | 8904 | 17808 | 530 | 1060 | RAVEL, GE | 4 | 35616 | 2120
22 | SITC of Electronic Hooter cum Flasher | NOS | 1 | 1 | 2 | 2342.6 | 4685.2 | 212 | 424 | RAVEL, | 2 | 4685.2 | 424
23 | 2C x 1.5 mm2, Stranded Copper conductor,Type A ST1 PVC insulated, Armoured FRLS Cable 1100 V as per IS 1554, with GI saddle spacers every 0.3 mtr with Single compression Cable Glands, MS POWDER COATED Junction Boxes (wherever required), terminals, Ferruling complete. | Mtrs | 120 | 120 | 240 | 84.8 | 20352 | 37.1 | 8904 | POLYCAB / VARSHA/ KEI/DATA FLEX | 248 | 21030.4 | 9200.8
24 | Conducting 'room integrity' test using door fan test methodology. This test should use small pressure differentials between the enclosure and surrounding areas by locating the fan equipment in ups and battery rooms doorway. Pressure and airflow measurements to be taken, from which the leakage characteristics of the enclosure to be established. The predicted retention time to be calculated from these leakage characteristics and the enclosure and extinguishing system data. The door fan test methodology should be in accordance with the general requirements specified in BS 5306, BS:ISO 14520, NFPA 12A, NFPA 2001 and the BFPSA Code of Practice for Gaseous Extinguishing Systems. Vendor to conduct detailed visual check to ascertain readiness of the room for test. During test, if any leak found the same shall be attended by Civil vendor. After rectification, the test has to be repeated till successful completion. | Lot | 1 | 1 | 2 | 0 | 0 | 77500 | 155000 | JOB |  | 0 | 0
25 | Providing fire sealant all around the room for the services entry | Lot | 1 | 1 | 2 | 12720 | 25440 | 1590 | 3180 | Hilti/Promat/3M |  | 0 | 0
| TOTAL WITHOUT TAX | [5 empty] | 744757.0337 |  | 230397.8 |  |  | 645275 | 68677.4 | 99482.0337 | 161720.4
NOTE:-
PROVIDE SEALANTS FOR ALL THE SERVICE CROSSOVERS. ROOM HAS TO BE COMPELTELY SEALED.

## Design calculation
UL Listed - NOVAC (Fluoro Ketone) Suppression System - Design
Client |  | E Sollutions Consultancy Pvt Ltd., Chennai. | [7 empty] | Hazard Type | [5 empty] | Class | A / C
[10 empty] | Des. Concentration | [5 empty] | % V / V | 4.5
Project |  | CMRL | [7 empty] | Des. Temperature | [5 empty] | Deg.° C | 21
[10 empty] | Des. Pressure | [5 empty] | Bar | 25 |  | Width in M./ Area Sq.m.
S.No. | Room Protected | Dimensions | [13 empty] | Cylinder in Ltrs. | Cylinder Qty | Fill Density Kg/Ltr.
|  | Area Sq.m. | Height in M. |  |  | Volume in M3 |  |  |  | Nozzles |  |  |  | Gas Qty Kgs.
|  |  | CV | RV | FV | CV | RV | FV | Total | CV | RV | FV | Total | Actual | Stored
1 | Server Room | 13 | 0.9 | 2.15 | 0.45 | 11.7 | 27.95 | 5.85 | 45.5 | 1 | 1 | 1 | 3 | 29.7139 | 30.4568 | 80 | 1 | 0.38071
2 | UPS & Battery Room | 17 | 0.9 | 2.15 | 0.45 | 15.3 | 36.55 | 7.65 | 59.5 | 2 | 2 | 2 | 6 | 38.8567 | 39.8281 | 80 | 1 | 0.49785
| Total Qty | [11 empty] | 9 |  | 70.2849 |  | 2

## PHE
PHE SYSTEM BOQ
Sl. No. | System | Amount | Remark
A | SANITARY WARES AND ACCESSORIES | 825866
B | INTERNAL DRAINAGE & WATER SUPPLY PIPES & FITTINGS | 1308545
| GRAND TOTAL | 2134411
Sl. No. | Description | Unit | Qty | Rate (INR) |  | Amount (INR)
|  |  |  | Supply | Installation | Supply | Installation
A | TOILET - SANITARY WARES AND ACCESSORIES
The work shall include cutting making of walls and floors etc. The rates quoted shall include cost of necessary consumables like brass screws, CP extension nipple of approved make, dia and length, wooden plugs, white cement, sealants etc. Only drilling machines shall be used for making the holes in the walls for fixing, no wall jumper and hammer will be allowed.
1 | Supply ,Installing, testing and commissioning of White color wall mounted European water closet with concealed dual flush tank with necessary pan connecter, bend,checknut, angle cock, solid seat cover with polythene buffer and flap, CP flanges etc.,complete. | Nos | 11 | 15432.9712 | 2120 | 169762.6831 | 23320
| Make : Jaquar |  |  | 0 | 0
| Model : Closet - CNS - WHT - 963SPP |  |  | 0 | 0
| Concealed flush tank - JCS-WHT-2400FS |  |  | 0 | 0
| Flush plates - JCP-CHR-152415 |  |  | 0 | 0
|  |  |  | 0 | 0
2 | Supply, Installing, testing and commissioning of handicapped toilet including water closet, flush valve for closet, rectangular wall hung wash basin, 15mm dia Pillar cock with waste coupling, CP angle cock, 32mm dia CP bottle trap with extension pipe, grab bar, supporting bracket with necessary steel to support basin, 450mm long CP connection pipe and CP wall flanges all of approved make etc.,complete. | Nos | 1 | 28480.5381 | 3710 | 28480.5381 | 3710
|  |  |  | 0 | 0
3 | Supply, fixing, testing and commissioning of 15 mm CP health faucet of approved make with necessary CP flexible hose 1000 mm flexible tube, 15mm dia brass C.P. Angle stop cock with flange, CP wall flange etc., complete. | Nos | 12 | 1196.9466 | 318 | 14363.3593 | 3816
| Make / Model : Jaquar / Health faucet -ALD- CHR- 573 |  |  | 0 | 0
| Angle cock - 5053 N |  |  | 0 | 0
|  |  |  | 0 | 0
4 | Supplying, installing, testing and commissioning White Vitreous large flat back urinal with sensor flush valve supported by CI/GI bracket duly painted, including CP brass waste with dome type grating, CP cast brass bottle trap with extension piece, wall flanges, automatic flushing systems for urinal to ensure flushing only immediately after use, comprising of all plumbing, electronic and electrical items. , CP wall flange, infrared photo cells (Sensor), eyes electrically operated solenoid valve, step down transformer/equipment and any other item required to provide satisfactory functioning. | Nos | 5 | 16332.8034 | 1060 | 81664.0169 | 5300
| Make / Model : Jaquar / Urinal - URS-WHT-13263 |  |  | 0 | 0
| sensor flush valve - SNR-CHR-51097 |  |  | 0 | 0
|  |  |  | 0 | 0
5 | Fixing & testing of curved shaped urinal partition with frosted glass including providing & fixing concealed CI bracket, cutting and making good. | Nos | 4 | 4219.0246 | 954 | 16876.0983 | 3816 | 8mm thick glass considered - as per the query response.
| Make / Model : Jaquar / Urinal partition- 1810-UC/1110UC |  |  | 0 | 0
|  |  |  | 0 | 0 |  | 0
6 | Supply, Installing, testing and commissioning of under counter wash basin, 15mm dia sensor Pillar cock and waste coupling, 32mm dia CP bottle trap with extension pipe, supporting bracket with necessary steel to support basin 1 No.15mm CP angle valve with 450mm long CP connection pipe and CP wall flanges all of approved make etc.,complete. | Nos | 12 | 13047.5669 | 2120 | 156570.8034 | 25440
| Make : Jaquar |  |  | 0 | 0
| Model : Wash Basin - FNS-WHT-40701 |  |  | 0 | 0
| Sensor Pillar cock - SNR-CHR-35019PMEB |  |  | 0 | 0
| Angle cock - 5053N |  |  | 0 | 0
| Bottle trap - ALD 769 |  |  | 0 | 0
| Waste coupling - ALD 705 |  |  | 0 | 0
|  |  |  | 0 | 0
7 | Supply, installation and fixing of stainless steel toilet paper holder with SS screws on the wall. | Nos | 12 | 967.7441 | 318 | 11612.9288 | 3816
| Make / Model : Jaquar / CAN-CHR-1153S |  |  | 0 | 0
|  |  |  | 0 | 0
8 | Supply, installation and fixing of stainless steel body paper towel dispenser with SS screws on the breakout wall. (Cabinet : 18-8 stainless steel 304, Capacity : 450 (M & Z fold), 600 multifold) | Nos | 7 | 4081 | 530 | 28567 | 3710
| Make : Kimberly - 49807 |  |  | 0 | 0
|  |  |  | 0 | 0
9 | Supply, installation and fixing of Robe hook with PVC rawl plug & C.P. brass screw complete as required. | Nos | 12 | 441.4271 | 159 | 5297.1254 | 1908
| Make / Model : Jaquar / ACN-CHR-1161N |  |  | 0 | 0
|  |  |  | 0 | 0
10 | Supply, installation and fixing of stainless steel body liquid soap dispenser with PVC rawl plug & C.P. brass screw complete as required. (Material : SS 304, Dispense : Foam soap, Battery : 4 x AA alkaline duracell, sensing distance : 5-9cm, Dispense volume : 1-2ml) | Nos | 7 | 4187 | 265 | 29309 | 1855
| Make : Euronics -ES802F |  |  | 0 | 0
|  |  |  | 0 | 0
11 | Supply and fixing of Wall mounted SS body Hand Dryer with SS screws on the wall. (Auto cutoff : 30sec, Sensor range : 12 cm - 15 cm, Hand dry time : less than 20 secs, Motor ; Brush type, dual ball bearings, Speed : 25,000 RPM, Rated power : 550 W, Current ; 2.5 A, Blowing volume : > 270 cum/hr, Air speed : 95 m/s , Operation : Touch free infra red activation) | Nos | 7 | 15370 | 530 | 107590 | 3710
| Make : Euronics - EH 26 |  |  | 0 | 0
|  |  |  | 0 | 0
12 | Supply, installation and fixing approved make Mirror with suitable size for Single and combined wash basin's necessary fixing screws etc complete. | Nos | QRO | 9540 | 530
|  |  |  | 0 | 0
13 | Supply and fixing of waste Chute | Nos | QRO | 3710 | 318
|  |  |  | 0 | 0
14 | Supply and fixing of ABS body Aerosol Fragrance Dispensor (Material : Polycarbonate ABS casing, Battery : 2 X D size alkaline batteries, Spray interval ; 5, 10, 15, 30mins, Option : Day / Night / 24hrs, Refill can ; 300 ML) | Nos | QRO | 1584.7 | 318
| Make : Euronics - EA 24 |  |  | 0 | 0
|  |  |  | 0 | 0
15 | Supply, Installing, testing and commissioning of stainless steel sink with drain board , with 15m dia CP sink Cock , CP waste coupling, 32mm dia CP bottle trap with extension pipe, supporting CI bracket to support sink, and CP wall flanges, all complete set of approved make. | Nos | QRO | 25970 | 2650
| Make :Hafelei Stainless Steel splash Sink |  |  | 0 | 0
| Angle cock Make & Model : 5053N |  |  | 0 | 0
| CP Bottle trap Make & Model : Jaquar & ALT-CHR-769L300x190 |  |  | 0 | 0
| CP waste coupling Make & Model : Jaquar & ALD-709, |  |  | 0 | 0
| Hot & cold tap with mixer Make & Model : Jaquar & QQP-7309PM with flow restrictor(1.4LPM) |  |  | 0 | 0
|  |  |  | 0 | 0
16 | Supply, Installing, testing and commissioning of stainless steel sink without drain board , with 15m dia CP sink Cock , CP waste coupling, 32mm dia CP bottle trap with extension pipe, supporting CI bracket to support sink, and CP wall flanges, all complete set of approved make. (Juice counter) | Nos | 3 | 13287.1 | 2650 | 39861.3 | 7950
| Model : Hindware-Sink-Domingo 18x16x9 with waste coupling |  |  | 0 | 0
| Make / Model : hindware Angle cock - Cat. No.: F850077 Angular Stop Cock with Wall Flange |  |  | 0 | 0
| Bottle trap - F850072 300 mm & 250 mm |  |  | 0 | 0
| Make / Model : hindware Cat. No.: F690058ARI-CHR-39347S Sink cock |  |  | 0 | 0
|  |  |  | 0 | 0
17 | Supply, iinstallation and fixing testing and commissioning of apparoved make electically operated storage water heater inner container made from copper or stainless steel including the remal instalation safety valve, vacuum relief valve, neon lamp, mounting brackets, angle valve, connection hose installing in position with coach screws or bolts, nuts, testing, commissioning, etc, complete. |  |  | 0 | 0
| Make / Model : jaquar / Erica vertical / horizontal | Nos | 2 | 16430 | 530 | 32860 | 1060
| a) 25 ltrs (For Casfeteria) |  |  | 0 | 0
| 2nos Angle cock Make & Model : 5053N |  |  | 0 | 0
|  |  |  | 0 | 0
18 | Supply, iinstallation and fixing testing and commissioning of apparoved make completed shower set including wall mixer with diverter, shower arm with sliding Shower rose on a vertical rail. | Nos | 1 | 10990.2727 | 2650 | 10990.2727 | 2650
| Make : JAQUAR |  |  | 0 | 0
| SHOWER ARM : SHA-CHR-49483 |  |  | 0 | 0
| OVERHEAD SHOWER : OHS-CHR-1623 |  |  | 0 | 0
| EXPOSED PART KIT OF SINGLE LEVER : OPP-CHR-15079NKPM |  |  | 0 | 0
| BATH SPOUT WITH WALL FLANGE : SPJ-CHR-15429PM |  |  | 0 | 0
| Sub - Total |  |  |  |  | 733805.1261 | 92061
| Grand Total - SANITARY WARES AND ACCESSORIES | [5 empty] | 825866
Sl. No. | Description | UoM | Total Qty | Rate (INR) |  | Amount (INR)
|  |  |  | Supply | Installation | Supply | Installation
B | INTERNAL DRAINAGE & WATER SUPPLY PIPES & FITTINGS
1 | Supplying, fixing, testing & commissioning of Waste & vent pipes of centrifugally spun cast iron pipe as per IS:3989 including all fittings like bend, tees, elbows, collars, junction inspection doors, cowls, offsets, access pipes, CI pipe connection with flange adapter or humbles joints, etc. joining with epoxy sealant joints after packing with hemp including finishing etc. complete. (INTERNAL/SUSPENDED PIPING)
| a)40mm dia | Rmt | 20 | 883.3333 | 196.2963 | 17666.6667 | 3925.9259
| b)50mm dia | Rmt | 20 | 1079.6296 | 196.2963 | 21592.5926 | 3925.9259
| c)75mm dia | Rmt | 70 | 1374.0741 | 196.2963 | 96185.1852 | 13740.7407
| d)110mm dia | Rmt | 40 | 1472.2222 | 196.2963 | 58888.8889 | 7851.8519
|  |  |  | 0 | 0
2 | Supplying, fixing, testing & commissioning of special C.I Multi floor trap / P trap with necessary connection of 100mm dia inlet and 75mm dia outlet fixed on a bed of cement concrete etc.. Complete. ( The frame and grating shall be approved by architect) | Nos | 21 | 1962.963 | 196.2963 | 41222.2222 | 4122.2222
|  |  |  | 0 | 0
3 | Supply and fixing of cockroach trap of size 153mm x 153mm, complete as per specifications. (The item rate shall include all costs towards labour, tools, tackles & machineries, all leads & lifts, work related cleaning) complete | Nos | 21 | 2453.7037 | 196.2963 | 51527.7778 | 4122.2222
|  |  |  | 0 | 0
4 | Supply, fixing and testing of CI ceiling clean out . For removing Clogging, etc., complete.(The frame and grating shall be approved by Architects) | Nos | QRO | 4416.6667 | 343.5185
|  |  |  | 0 | 0
5 | Supply, fixing and testing of CI floor clean out (110mmx110mm). For removing Clogging, etc., complete.(The frame and grating shall be approved by Architects) |  |  | 0 | 0
a | 75mm dia | Nos | 4 | 1177.7778 | 196.2963 | 4711.1111 | 785.1852
b | 110mm dia | Nos | 4 | 1472.2222 | 196.2963 | 5888.8889 | 785.1852
|  |  |  | 0 | 0
6 | Supplying and fixing testing & commissioning of Galvanized Iron Pipes of ISI marked, I.S.1239 ('C' Class) including all G.I. Heavy duty Fittings like tees, elbows, bends, of approved make, threading, cutting, jointing & testing. Making hole openings in walls & floors. Providing galvanized steel brackets, channels, angles, flats, anchor fasteners, clamps, threaded rods, nuts, bolts washers etc. to complete the work and making good walls & floors etc., complete. Painting the exposed G.I. pipes with Two coat of zinc chromate primer with two coats of synthetic enamel paint of approved colour / shade etc., complete. |  |  | 0 | 0
| (Pipe running on ceiling, inside the wall concealed for cold & hot water supply) |  |  | 0 | 0
| a) 20 mm dia | Rmt | 90 | 883.3333 | 294.4444 | 79500 | 26500
| b) 25 mm dia | Rmt | 30 | 932.4074 | 294.4444 | 27972.2222 | 8833.3333
| c) 32 mm dia | Rmt | 25 | 1128.7037 | 294.4444 | 28217.5926 | 7361.1111
| d) 40 mm dia | Rmt | 30 | 1275.9259 | 294.4444 | 38277.7778 | 8833.3333
| e) 50 mm dia | Rmt | QRO | 1619.4444 | 294.4444
|  |  |  | 0 | 0
7 | Providing & fixing of CPVC pipes confirming to IS 15778:2007 ASTM D-2846 standard including all CPVC fittings like tees, elbows, bends, unions, coupling, reducer tees, collars etc. The work shall include cutting jointing with solvent cement pressure testing the joints / pipeline for 10 kg/sq.cm hydraulic pressure, for 10 hours etc. making holes, including chasing in solid block masonry walls with groove cutting machine to required width and depth, making bores in walls, foundations and RCC slabs, making good the walls and bores in CC or CM 1:3 as applicable clearing the debris, grouting of concealed pipes, MS hooks for fixing pipes and making good the walls and floors. |  |  | 0 | 0
| Note: Strictly use SDR-11 grade - CPVC pipe and fittings for internal cold & hot water supply |  |  | 0 | 0
| Note: Rate Quoted shall be inclusive of cost of other consumables like hacksaw blade, solvent for CPVC pipe |  |  | 0 | 0
| (Pipe running on ceiling, inside the wall concealed for cold, flushing & hot water supply) |  |  | 0 | 0
| (Consealed pipes) |  |  | 0 | 0
| a) 20 mm dia | Rmt | 60 | 932.4074 | 294.4444 | 55944.4444 | 17666.6667
| b) 25 mm dia | Rmt | 5 | 1079.6296 | 294.4444 | 5398.1481 | 1472.2222
| c) 32 mm dia | Rmt | QRO | 0 | 0
| d) 40 mm dia | Rmt | QRO | 0 | 0
| e) 50 mm dia | Rmt | QRO | 0 | 0
| (Ceiling transfer pipes) - Option |  |  | 0 | 0
| a) 20 mm dia | Rmt | 90 | 422.037 | 152.1296 | 37983.3333 | 13691.6667
| b) 25 mm dia | Rmt | 30 | 618.3333 | 186.4815 | 18550 | 5594.4444
| c) 32 mm dia | Rmt | 25 | 809.7222 | 215.9259 | 20243.0556 | 5398.1481
| d) 40 mm dia | Rmt | 30 | 1084.537 | 255.1852 | 32536.1111 | 7655.5556
| e) 50 mm dia | Rmt | QRO | 0 | 0
|  |  |  | 0 | 0
8 | Providing and fixing of proprietary polyshield outer mechanical protection on nitrle rubber Insulation comprising of wrapping with poly glass tape helically wound and subsequently applying 2 coats of polyshield material (resin & hardner) as per manufacturers specification and approved by Project Manager / Consultnats. |  |  | 0 | 0
| a) 20 mm dia | Rmt | 10 | 1177.7778 | 294.4444 | 11777.7778 | 2944.4444
| b) 25 mm dia | Rmt | QRO | 0 | 0
| c) 32 mm dia | Rmt | QRO | 0 | 0
|  |  |  | 0 | 0
9 | Supply and fixing of lever operated Brass / Gun metal ball valve of approved make , complete. The valve shall be fixed after the union of PVC. The quoted rate shall also include the cost of the union, nipples etc., complete. The cost to includes joints required for the GI pipes to valves such as couplings etc., complete. |  |  | 0 | 0
| a) 20 mm dia (Screwed ends) | Nos | 14 | 3435.1852 | 490.7407 | 48092.5926 | 6870.3704
| b) 25 mm dia (Screwed ends) | Nos | 1 | 3925.9259 | 490.7407 | 3925.9259 | 490.7407
| c) 32 mm dia (Screwed ends) | Nos | 1 | 4416.6667 | 490.7407 | 4416.6667 | 490.7407
| c) 40 mm dia (Screwed ends) | Nos | 2 | 4907.4074 | 490.7407 | 9814.8148 | 981.4815
|  |  |  | 0 | 0
10 | Supplying, installing, fixing, jointing, testing and commissioning of Water Dispenser, Outlet of Hot, Cold , Warm. (Location - Cafeteria area) Bubble top type | Nos | QRO | 0 | 0
|  |  |  | 0 | 0
11 | Supplying, installing and testing approved make Electromagnetic flow water meter with BMS compatibility including 3 Nos Ball valves for isolation and By pass with unions etc., complete. | Nos |  | 0 | 0
| a) 20mm dia | Nos | QRO | 0 | 0
| b) 25mm dia | Nos | QRO | 0 | 0
| c) 40mm dia | Nos | 2 | 8342.5926 | 490.7407 | 16685.1852 | 981.4815
|  |  |  | 0 | 0
12 | Supplying and fixing drain lift-2 with collection tank, waste water transfer pumpset automatic control float, including tank, isolation valve NRV, control panel pumpset capable of discharging 1 LPS testing, commissioning, maintain the system for one year etc. complete. (To pump waste water to downtake pipe in PHE shaft (1 working + 1 standby) Interconnection ball valve & NRV including vendor scope - (Option) | Nos | 1 | 263940 | 24537.037 | 263940 | 24537.037
|  |  |  | 0 | 0
13 | Supply, Installing, testing and commissioning of approved make CPVC pipes as per ASTM D-2846 for grey water pumping from solo lift pumps to risers (SDR 11 grade) and pipe specials like Coupler, reducer, elbow, and brass male/ female threaded pipe specials , cutting the pipes, fixing the pipe specials using solvent cement solution supplied by the same manufacturer, making water tight joints, making holes in walls restoring the damaged portions to their original condition using required materials, providing suitable pipe clamps fixed to structural support, installing pipe work to perfect plumb, straight in horizontal, conducting hydraulic test to pipe work to a pressure of 7 Kg per Sq.cm, etc. complete and as directed by the site engineer. The rate should include noise insulation for all exposed pipes. |  |  | 0 | 0
| a)32mm dia | Rmt | QRO | 0 | 0
| b)40mm dia | Rmt | QRO | 0 | 0
|  |  |  | 0 | 0
14 | Supply & Installation of 150x60mm GI raceways with powder coat without cover made out of 16 SWG GI body to be installed below the drain pipes. RAL Colour shall be matched with Architect requirement. |  |  | 0 | 0
| a) 150mm x 60mm | Rmt | QRO | 0 | 0
| b) 300mm x 60mm | Rmt | QRO | 0 | 0
|  |  |  | 0 | 0
15 | Supply, fixing and testing of Garbodrain G-1000, including all fittings, should be anti-jam impellers made of SS 304 for efficient grinding & corrosion free, run with AC power supply with calling bell switch for dry run protection. (Juice counter) | Nos | 1 | 21200 | 981.4815 | 21200 | 981.4815
|  |  |  | 0 | 0
16 | Supply, fixing and testing of Garbodrain G-2000, including all fittings, should be anti-jam impellers made of SS 304 for efficient grinding & corrosion free, run with AC power supply with calling bell switch for dry run protection. (Hand wash & dish wash) | Nos | 2 | 51940 | 981.4815 | 103880 | 1962.963
| Sub - Total |  |  |  |  | 1126038.9815 | 182506.4815
| Grand Total - INTERNAL DRAINAGE & WATER SUPPLY PIPES & FITTINGS | [5 empty] | 1308545
The contractor shall supply all fixing items like extension nipples, teflon tape, white cement, putty, coach screws, fischer bolts etc., for fixing Sanitary fixtures and CP fittings. The quoted rate for fixing the said items shall include the supply of all the above indicated items.
Sl.No | Items | Approved makes
1 | Water closet, wash basin & urinal | Jaquar / Hindware / Roca / Parryware
2 | Concealed type cistern | Jaquar / Hindware / Roca / Parryware
3 | CP Fitting | Jaquar / Parryware / Roca / Hindware
4 | Hand drier & Dispenser | Euronics / kimberly clark
5 | Health Faucet | Jaquar / Parryware / Roca / Hindware
6 | Stainless steel sink | Hafele
7 | Ball Valve | Advance / Zoloto
8 | Flexible Connection | Metaflex / Tozen /Mason
9 | Pipe supports | Hitech / Chilly / Easyflex / Intellotech
10 | Cable | Polycab / Havells / Finolex
11 | CPVC Pipes & fittings | Astral / Ashirwad / Supreme
12 | GI Pipes & fittings | TATA / JINDAL
13 | CI pipes & fittings | BPL / INDO / BIC / BIF / JINDAL
14 | Water dispenser | Voltas / Oasis
15 | Water Heater | Jaquar / Erica